## COGEN_ISSUE_A (hidden)
I&C VALVE LIST
PROJECT : TANAJIB IPP
DOC NO. : 19K9-20CZF00-J22-0001
DESCRIPTION : I&C VALVE | [6 empty] | Bar.g로 변경 요 |  | Bar.g로 변경 / PSV Set P 값은 Barg 기준으로 혹시 변동사항 있는지 기계팀에 확인 문의드렸으며, 수정 필요 시 전달드리겠습니다.
NO. | P&ID | SYSTEM | TYPE | KKS TAG | DESCRIPTION | FLUID | DESIGN CONDITION |  | SET PRESSURE (BARG) | PDC | LINE SIZE | LINE SPEC | SPECIFICATION | [8 empty] | MAKER | MODEL NO. | REMARK
[7 empty] | PRESSURE INLET (BARG) | TEMP. (DEG.C) |  |  |  |  | ACTUATOR TYPE | BODY TYPE | FAIL POSITION | LEAKAGE CLASS | SIZE (DN) | BODY MATERIAL | TRIM MATERIAL | VALVE RATING | END CONNECTION
1 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 13LBA13AA201 | #13 HRSG STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA1 | 200 | BA1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 200 | SA217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
2 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 13LBA13AA204 | #13 HRSG HHP STEAM TO STARTUP BYPASS DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
3 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 13LBA10AA204 | #13 HRSG HHP MAIN STEAM DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
4 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 16LBA13AA201 | #16 AUX BOILER STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA1 | 150 | BA1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | SA217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
5 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 16LBA13AA204 | #16 AUX BOILER HHP STEAM TO STARTUP BYPASS DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
6 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 16LBA10AA204 | #16 AUX BOILER HHP MAIN STEAM DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
7 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 17LBA13AA201 | #17 AUX BOILER STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA1 | 150 | BA1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | SA217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
8 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 17LBA13AA204 | #17 AUX BOILER HHP STEAM TO STARTUP BYPASS DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
9 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 17LBA10AA204 | #17 AUX BOILER HHP MAIN STEAM DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
10 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 21LBA10AA204 | #21 HHP STEAM HEADER DRAIN MOV 1 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
11 | 19K9-20LBA10-M05-0001 | HHP STEAM SYSTEM | MOV | 22LBA10AA204 | #22 HHP STEAM HEADER DRAIN MOV 1 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
12 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 14LBA13AA201 | #14 HRSG STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA1 | 200 | BA1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 200 | SA217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
13 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 14LBA13AA204 | #14 HRSG HHP STEAM TO STARTUP BYPASS DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
14 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 14LBA10AA204 | #14 HRSG HHP MAIN STEAM DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
15 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 15LBA13AA201 | #15 HRSG STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA1 | 200 | BA1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 200 | SA217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
16 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 15LBA13AA204 | #15 HRSG HHP STEAM TO STARTUP BYPASS DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
17 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 15LBA10AA204 | #15 HRSG HHP MAIN STEAM DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
18 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 21LBA10AA208 | #21 HHP STEAM HEADER DRAIN MOV 2 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
19 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 21LBA10AA214 | #21 HHP STEAM HEADER DRAIN MOV 3 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
20 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 22LBA10AA208 | #22 HHP STEAM HEADER DRAIN MOV 2 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
21 | 19K9-20LBA10-M05-0002 | HHP STEAM SYSTEM | MOV | 22LBA10AA214 | #22 HHP STEAM HEADER DRAIN MOV 3 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
22 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA15AA201 | #11 ST STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA2 | 200 | BA2 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 200 | A217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
23 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA15AA202 | ST STARTUP BYPASS STEAM TO #11 STG DRAIN MOV | STEAM | 147 | 574 | N/A | LBA2 | 25 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 25 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
24 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA10AA201 | #11 ST HHP STEAM ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA2 | 400 | BA2 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 400 | A217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
25 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA10AA204 | HHP STEAM HEADER TO #11 STG INLET DRAIN MOV 1 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
26 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA10AA208 | HHP STEAM HEADER TO #11 STG INLET DRAIN MOV 2 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
27 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA10AA214 | HHP STEAM HEADER TO #11 STG INLET DRAIN MOV 3 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
28 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBA10AA202 | HHP STEAM HEADER TO #11 STG INLET DRAIN MOV 4 | STEAM | 147 | 574 | N/A | LBA2 | 50 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
29 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBR10AA202 | HP STEAM HEADER TO #11 STG INLET DRAIN MOV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 25 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 25 | A105 | 13CR/STL | 600 | SW | LATER | LATER
30 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBD10AA202 | #11 STG EXTRACTION TO #21 LP STEAM HEADER DRAIN MOV 1 | STEAM | 9.7 | 253.1 | N/A | LBD1 | 50 | HB2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
31 | 19K9-20LBA10-M05-0003 | HHP STEAM SYSTEM | MOV | 11LBD10AA201 | #11 STG EXTRACTION TO #21 LP STEAM HEADER DRAIN MOV 2 | STEAM | 9.7 | 253.1 | N/A | LBD2 | 50 | HB2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
32 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA15AA201 | #12 ST STARTUP BYPASS ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA2 | 200 | BA2 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 200 | A217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
33 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA15AA202 | ST STARTUP BYPASS STEAM TO #12 STG DRAIN MOV | STEAM | 147 | 574 | N/A | LBA2 | 25 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 25 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
34 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA10AA201 | #12 ST HHP STEAM ISOLATION MOV | STEAM | 147 | 574 | N/A | LBA2 | 400 | BA2 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 400 | A217-C12A | 17CR/STL | 2500 | BW | LATER | LATER
35 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA10AA204 | HHP STEAM HEADER TO #12 STG INLET DRAIN MOV 1 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
36 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA10AA208 | HHP STEAM HEADER TO #12 STG INLET DRAIN MOV 2 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
37 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA10AA214 | HHP STEAM HEADER TO #12 STG INLET DRAIN MOV 3 | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
38 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBA10AA202 | HHP STEAM HEADER TO #12 STG INLET DRAIN MOV 4 | STEAM | 147 | 574 | N/A | LBA2 | 50 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
39 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBR10AA202 | HP STEAM HEADER TO #12 STG INLET DRAIN MOV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 25 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 25 | A105 | 13CR/STL | 600 | SW | LATER | LATER
40 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBD10AA202 | #12 STG EXTRACTION TO #22 LP STEAM HEADER DRAIN MOV 1 | STEAM | 9.7 | 253.1 | N/A | LBD1 | 50 | HB2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
41 | 19K9-20LBA10-M05-0004 | HHP STEAM SYSTEM | MOV | 12LBD10AA201 | #12 STG EXTRACTION TO #22 LP STEAM HEADER DRAIN MOV 2 | STEAM | 9.7 | 253.1 | N/A | LBD2 | 50 | HB2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
42 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 11LBR10AA201 | #21 HP STEAM HEADER ISOLATION MOV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 250 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 250 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
43 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | PSV | 21LBR10AA191 | #21 HP STEAM HEADER PSV | STEAM | 50.3 | 399 | 50.3 | LBR1 | IN : 200 / OUT : 250 | FB1 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 200 / OUT : 250 | A216-WCB | 316SS | 600 | RF | LATER | LATER
44 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 21LBR10AA203 | #21 HP STEAM HEADER DRAIN MOV 1 | STEAM | LATER | LATER | N/A | LBR10 | 40 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A105 | 13CR/STL | 600 | SW | LATER | LATER
45 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 21LBR10AA207 | #21 HP STEAM HEADER DRAIN MOV 2 | STEAM | LATER | LATER | N/A | LBR10 | 40 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A105 | 13CR/STL | 600 | SW | LATER | LATER
46 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 21LBR10AA201 | #21 HP STEAM HEADER FROM TGP ISOLATION MOV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 450 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 450 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
47 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 12LBR10AA201 | #22 HP STEAM HEADER ISOLATION MOV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 250 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 250 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
48 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | PSV | 22LBR10AA191 | #22 HP STEAM HEADER PSV | STEAM | 50.3 | 399 | 50.3 | LBR1 | IN : 200 / OUT : 250 | FB1 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 200 / OUT : 250 | A216-WCB | 316SS | 600 | RF | LATER | LATER
49 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 22LBR10AA203 | #22 HP STEAM HEADER DRAIN MOV 1 | STEAM | LATER | LATER | N/A | LBR10 | 40 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A105 | 13CR/STL | 600 | SW | LATER | LATER
50 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 22LBR10AA207 | #22 HP STEAM HEADER DRAIN MOV 2 | STEAM | LATER | LATER | N/A | LBR10 | 40 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A105 | 13CR/STL | 600 | SW | LATER | LATER
51 | 19K9-20LBR10-M05-0001 | HP STEAM HEADER SYSTEM | MOV | 22LBR10AA201 | #22 HP STEAM HEADER FROM TGP ISOLATION MOV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 450 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 450 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
52 | 19K9-20LBA30-M05-0001 | HRSG LP STEAM SYSTEM | MOV | 13LBA30AA201 | #13 HRSG LP STEAM DRAIN MOV | STEAM | LATER | LATER | N/A | LATER | LATER | LATER | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | LATER | LATER | LATER | LATER | LATER | LATER | LATER
53 | 19K9-20LBA30-M05-0001 | HRSG LP STEAM SYSTEM | MOV | 14LBA30AA201 | #14 HRSG LP STEAM DRAIN MOV | STEAM | LATER | LATER | N/A | LATER | LATER | LATER | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | LATER | LATER | LATER | LATER | LATER | LATER | LATER
54 | 19K9-20LBA30-M05-0001 | HRSG LP STEAM SYSTEM | MOV | 15LBA30AA201 | #15 HRSG LP STEAM DRAIN MOV | STEAM | LATER | LATER | N/A | LATER | LATER | LATER | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | LATER | LATER | LATER | LATER | LATER | LATER | LATER
55 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 21NAA10AA191 | #21 LP STEAM HEADER PSV 1 | STEAM | 9.7 | 253 | 9.5 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
56 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 21NAA10AA192 | #21 LP STEAM HEADER PSV 2 | STEAM | 9.7 | 253 | 9.5 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
57 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 21NAA10AA193 | #21 LP STEAM HEADER PSV 3 | STEAM | 9.7 | 253 | 9.7 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
58 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 21NAA10AA194 | #21 LP STEAM HEADER PSV 4 | STEAM | 9.7 | 253 | 9.7 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
59 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 21NAA10AA195 | #21 LP STEAM HEADER PSV 5 | STEAM | 9.7 | 253 | 9.7 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
60 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 22NAA10AA191 | #22 LP STEAM HEADER PSV 1 | STEAM | 9.7 | 253 | 9.5 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
61 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 22NAA10AA192 | #22 LP STEAM HEADER PSV 2 | STEAM | 9.7 | 253 | 9.5 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
62 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 22NAA10AA193 | #22 LP STEAM HEADER PSV 3 | STEAM | 9.7 | 253 | 9.7 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
63 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 22NAA10AA194 | #22 LP STEAM HEADER PSV 4 | STEAM | 9.7 | 253 | 9.7 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
64 | 19K9-20NAA10-M05-0001 | LP STEAM HEADER SYSTEM | PSV | 22NAA10AA195 | #22 LP STEAM HEADER PSV 5 | STEAM | 9.7 | 253 | 9.7 | NAA1 | LATER | HB2 | SELF ACTUATING | ANGLE | N/A | N/A | Bidder to proposal | A216-WCB | 316SS | 600 | RF | LATER | LATER
65 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | CV | 21NAA10AA101 | #21 LP STEAM HEADER PCV | STEAM | LATER | LATER | N/A | LATER | LATER | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | LATER | CLASS IV | LATER | LATER | LATER | LATER | LATER | LATER | LATER
66 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | CV | 22NAA10AA101 | #22 LP STEAM HEADER PCV | STEAM | LATER | LATER | N/A | LATER | LATER | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | LATER | CLASS IV | LATER | LATER | LATER | LATER | LATER | LATER | LATER
67 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | MOV | 21NAA10AA203 | #21 LP STEAM HEADER DRAIN MOV | STEAM | 9.7 | 253.1 | N/A | NAA10 | 50 | HB2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
68 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | MOV | 21NAA10AA201 | #21 LP STEAM HEADER TO TGP ISOLATION MOV | STEAM | 9.7 | 253.1 | N/A | NAA1 | 1300 | HB2 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 1300 | A216-WCB | 13CR/STL | 150 | BW | LATER | LATER
69 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | MOV | 22NAA10AA203 | #22 LP STEAM HEADER DRAIN MOV | STEAM | 9.7 | 253.1 | N/A | NAA10 | 50 | HB2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
70 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | MOV | 22NAA10AA201 | #22 LP STEAM HEADER TO TGP ISOLATION MOV | STEAM | 9.7 | 253.1 | N/A | NAA1 | 1300 | HB2 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 1300 | A216-WCB | 13CR/STL | 150 | BW | LATER | LATER
71 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | CV | 21LBR13AA101 | #21 HP STEAM HEADER TO AUX STEAM HEADER PCV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 80 | FB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
72 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | MOV | 21LBR13AA203 | #21 HP STEAM HEADER TO AUX STEAM HEADER DRAIN MOV | STEAM | LATER | LATER | N/A | LBR10 | 25 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 25 | A105 | 13CR/STL | 600 | SW | LATER | LATER
73 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | PSV | 21LBG00AA191 | #21 HP STEAM HEADER TO AUX STEAM HEADER PSV | STEAM | 12 | 330 | 13 | LBG1 | IN : 100 / OUT : 150 | GB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 100 / OUT : 150 | A216-WCB | 316SS | 600 | RF | LATER | LATER
74 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | MOV | 22LBR13AA203 | #22 HP STEAM HEADER TO AUX STEAM HEADER DRAIN MOV | STEAM | LATER | LATER | N/A | LBR10 | 25 | FB1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 25 | A105 | 13CR/STL | 600 | SW | LATER | LATER
75 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | CV | 22LBR13AA101 | #22 HP STEAM HEADER TO AUX STEAM HEADER PCV | STEAM | 50.3 | 398.9 | N/A | LBR1 | 80 | FB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
76 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | PSV | 22LBG00AA191 | #22 HP STEAM HEADER TO AUX STEAM HEADER PSV | STEAM | 12 | 330 | 13 | LBG1 | IN : 100 / OUT : 150 | GB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 100 / OUT : 150 | A216-WCB | 316SS | 600 | RF | LATER | LATER
77 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | MOV | 11LBG20AA201 | AUX STEAM TO #11 ST SEAL STEAM DRAIN MOV | STEAM | 12 | 330 | N/A | LBG1 | 50 | GB4 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL OPEN | CLASS IV | 50 | LATER | LATER | LATER | LATER | LATER | LATER
78 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | MOV | 12LBG20AA201 | AUX STEAM TO #12 ST SEAL STEAM DRAIN MOV | STEAM | 12 | 330 | N/A | LBG1 | 50 | GB4 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL OPEN | CLASS IV | 50 | LATER | LATER | LATER | LATER | LATER | LATER
79 | 19K9-20LBA40-M05-0004 | STEAM BYPASS AND LETDOWN SYSTEM | MOV | 20LBA11AA204 | #11 HRSG HHP AND AUX BOILER STARTUP BYPASS STATION DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
80 | 19K9-20LBA40-M05-0004 | STEAM BYPASS AND LETDOWN SYSTEM | MOV | 20LBA12AA204 | #12 HRSG HHP AND AUX BOILER STARTUP BYPASS STATION DRAIN MOV | STEAM | 147 | 574 | N/A | LBA10 | 40 | BA2 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 40 | A182-F91 | 17CR/STL | 2500 | SW | LATER | LATER
81 | 19K9-11MAL10-M05-0001 | ST DRAIN SYSTEM - UNIT 11 | MOV | 11LCW21AA201 | #11 FLASH TANK SPRAY WATER MOV | WATER | 4 | 100 | N/A | LCW1 | 50 | HB3 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
82 | 19K9-12MAL10-M05-0001 | ST DRAIN SYSTEM - UNIT 12 | MOV | 12LCW21AA201 | #12 FLASH TANK SPRAY WATER MOV | WATER | 4 | 100 | N/A | LCW1 | 50 | HB3 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
83 | 19K9-11LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 11 | CV | 11GHB01AA101 | #11 CLEAN DRAIN TO WASTE WATER TREATMENT SYSTEM TCV | WATER | LATER | LATER | N/A | GHB1 | 150 | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | LATER | LATER | LATER | LATER | LATER | LATER
84 | 19K9-11LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 11 | MOV | 11LCM10AA202 | #11 CLEAN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCM2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
85 | 19K9-11LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 11 | MOV | 11LCM10AA201 | #11 CLEAN DRAIN TO CONDENSATE COLLECTING TANK ISOLATION MOV | WATER | LATER | LATER | N/A | LCM2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
86 | 19K9-12LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 12 | CV | 12GHB01AA101 | #12 CLEAN DRAIN TO WASTE WATER TREATMENT SYSTEM TCV | WATER | LATER | LATER | N/A | GHB1 | 150 | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | LATER | LATER | LATER | LATER | LATER | LATER
87 | 19K9-12LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 12 | MOV | 12LCM10AA202 | #12 CLEAN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCM2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
88 | 19K9-12LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 12 | MOV | 12LCM10AA201 | #12 CLEAN DRAIN TO CONDENSATE COLLECTING TANK ISOLATION MOV | WATER | LATER | LATER | N/A | LCM2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
89 | 19K9-13LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 13 | MOV | 13LCL10AA202 | #13 HRSG BLOWDOWN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCL2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
90 | 19K9-13LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 13 | MOV | 13LCL10AA201 | #13 HRSG BLOWDOWN DRAIN TO DEMINERALISATION PLANT ISOLATION MOV | WATER | LATER | LATER | N/A | LCL2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
91 | 19K9-14LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 14 | MOV | 14LCL10AA202 | #14 HRSG BLOWDOWN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCL2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
92 | 19K9-14LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 14 | MOV | 14LCL10AA201 | #14 HRSG BLOWDOWN DRAIN TO DEMINERALISATION PLANT ISOLATION MOV | WATER | LATER | LATER | N/A | LCL2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
93 | 19K9-15LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 15 | MOV | 15LCL10AA202 | #15 HRSG BLOWDOWN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCL2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
94 | 19K9-15LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 15 | MOV | 15LCL10AA201 | #15 HRSG BLOWDOWN DRAIN TO DEMINERALISATION PLANT ISOLATION MOV | WATER | LATER | LATER | N/A | LCL2 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
95 | 19K9-16LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 16 | MOV | 16LCL10AA202 | #16 AUX BOILER BLOWDOWN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCL2 | 80 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
96 | 19K9-16LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 16 | MOV | 16LCL10AA201 | #16 AUX BOILER BLOWDOWN DRAIN TO DEMINERALISATION PLANT ISOLATION MOV | WATER | LATER | LATER | N/A | LCL2 | 80 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
97 | 19K9-17LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 17 | MOV | 17LCL10AA202 | #17 AUX BOILER BLOWDOWN DRAIN TO WASTE WATER TREATMENT SYSTEM MOV | WATER | LATER | LATER | N/A | LCL2 | 80 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
98 | 19K9-17LCL10-M05-0001 | BLOWDOWN & QUENCHING SYSTEM - UNIT 17 | MOV | 17LCL10AA201 | #17 AUX BOILER BLOWDOWN DRAIN TO DEMINERALISATION PLANT ISOLATION MOV | WATER | LATER | LATER | N/A | LCL2 | 80 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
99 | 19K9-11LCA10-M05-0001 | CONDENSATE SYSTEM - UNIT 11 | CV | 11GHC01AA101 | #11 AIR COOLED CONDENSER CONDENSATE COLLECTION TANK INITIAL FILL & ENERGENCY MAKEUP LCV | WATER | LATER | LATER | N/A | GHC4 | 100 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 100 | A351-CF8 | SS304 | 150 | BW | LATER | LATER
100 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | PRV | 11LCW11AA701 | #11 FLASH TANK SPRAY AND VACUUM BREAKER SEAL WATER PRV | WATER | 4 | 100 | 13 | LCA2 | 50 | GB2 | SELF ACTUATING | GLOBE | N/A | N/A | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
101 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | PSV | 11LCW21AA191 | #11 FLASH TANK SPRAY AND VACUUM BREAKER SEAL WATER PSV | WATER | 4 | 100 | 4 | LCW1 | IN : 25 / OUT : 25 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 25 | A105 | 316SS | 600 | RF | LATER | LATER
102 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | CV | 11LCA15AA101 | #11 CONDENSATE DUMP LCV | WATER | 17.987 | 100 | N/A | LCA2 | 80 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
103 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | CV | 11LCA14AA101 | #11 CEP MINIMUM RECIRCULATION FCV | WATER | 17.987 | 100 | N/A | LCA2 | 80 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
104 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | CV | 11LCA10AA101 | #11 CEP DISCHARGE HEADER AIR COOLED CONDENSER CONDENSATE COLLECTION TANK LCV | WATER | 17.987 | 100 | N/A | LCA2 | 250 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 250 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
105 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | MOV | 11LCA10AA201 | #11 CONDENSATE DISCHARGE HEADER ISOLATION MOV | WATER | 17.987 | 100 | N/A | LCA2 | 250 | GB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 250 | A216-WCB | A351-CF8 | 300 | LUG | LATER | LATER
106 | 19K9-12LCA10-M05-0001 | CONDENSATE SYSTEM - UNIT 12 | CV | 12GHC01AA101 | #12 AIR COOLED CONDENSER CONDENSATE COLLECTION TANK INITIAL FILL & ENERGENCY MAKEUP LCV | WATER | LATER | LATER | N/A | GHC4 | 100 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 100 | A351-CF8 | SS304 | 150 | BW | LATER | LATER
107 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | PRV | 12LCW11AA701 | #12 FLASH TANK SPRAY AND VACUUM BREAKER SEAL WATER PRV | WATER | 4 | 100 | 13 | LCA2 | 50 | GB2 | SELF ACTUATING | GLOBE | N/A | N/A | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
108 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | PSV | 12LCW21AA191 | #12 FLASH TANK SPRAY AND VACUUM BREAKER SEAL WATER PSV | WATER | 4 | 100 | 4 | LCW1 | IN : 25 / OUT : 25 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 25 | A105 | 316SS | 600 | RF | LATER | LATER
109 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | CV | 12LCA15AA101 | #12 CONDENSATE DUMP LCV | WATER | 17.987 | 100 | N/A | LCA2 | 80 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
110 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | CV | 12LCA14AA101 | #12 CEP MINIMUM RECIRCULATION FCV | WATER | 17.987 | 100 | N/A | LCA2 | 80 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
111 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | CV | 12LCA10AA101 | #12 CEP DISCHARGE HEADER AIR COOLED CONDENSER CONDENSATE COLLECTION TANK LCV | WATER | 17.987 | 100 | N/A | LCA2 | 250 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 250 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
112 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | MOV | 12LCA10AA201 | #12 CONDENSATE DISCHARGE HEADER ISOLATION MOV | WATER | 17.987 | 100 | N/A | LCA2 | 250 | GB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 250 | A216-WCB | A351-CF8 | 300 | LUG | LATER | LATER
113 | 19K9-20LCP10-M05-0001 | CODENSATE SYEYEM - COMMON | PSV | 20LCP03AA191 | HEAT EXCHANGER FOR CONDENSATE RETURN A TO CONDENSATE RETURN STORAGE TANK PSV | WATER | 14.5 & F.V | 65 | 14.5 | LCP3 | IN : 25 / OUT : 25 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 25 | A105 | 316SS | 600 | RF | LATER | LATER
114 | 19K9-20LCP10-M05-0001 | CODENSATE SYEYEM - COMMON | PSV | 20LCP04AA191 | HEAT EXCHANGER FOR CONDENSATE RETURN B TO CONDENSATE RETURN STORAGE TANK PSV | WATER | 14.5 & F.V | 65 | 14.5 | LCP3 | IN : 25 / OUT : 25 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 25 | A105 | 316SS | 600 | RF | LATER | LATER
115 | 19K9-20LCP10-M05-0001 | CODENSATE SYEYEM - COMMON | MOV | 20QCB01AA201 | OXYGEN SCAVENSER DOSING LINE MOV | WATER | LATER | LATER | N/A | LCP2 | 25 | HB3 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 25 | A105 | 13CR/STL | 600 | SW | LATER | LATER
116 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | MOV | 20LCP11AA201 | CONDENSATE RETURN STORAGE TANK A INLET ISOLATION MOV | WATER | 2.987 | 65 | N/A | LCP3 | 350 | HB3 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 350 | A216-WCB | A351-CF8 | 150 | LUG | LATER | LATER
117 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | MOV | 20LCP12AA201 | CONDENSATE RETURN STORAGE TANK B INLET ISOLATION MOV | WATER | 2.987 | 65 | N/A | LCP3 | 350 | HB3 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 350 | A216-WCB | A351-CF8 | 150 | LUG | LATER | LATER
118 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | CV | 20LCP30AA101 | CONDENSATE SUPPLY PUMP MINIMUM RECIRCULATION FCV | WATER | LATER | LATER | N/A | LCP5 | 250 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 250 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
119 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | CV | 20LCP31AA101 | CONDENSATE SUPPLY PUMP DISCHARGE HEADER PCV 1 | WATER | LATER | LATER | N/A | LCP5 | 450 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 450 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
120 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | CV | 20LCP32AA101 | CONDENSATE SUPPLY PUMP DISCHARGE HEADER PCV 2 | WATER | LATER | LATER | N/A | LCP5 | 450 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 450 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
121 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | MOV | 20LCP10AA201 | CONDENSATE RETURN STORAGE TANK TO STORM WATER LINE MOV | WATER | 2.987 | 65 | N/A | LCP3 | 150 | HB3 | MOTOR OPERATED (INCHING) | BUTTERFLY | FAIL LOCK | CLASS IV | 150 | A216-WCB | A351-CF8 | 150 | LUG | LATER | LATER
122 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | MOV | 20LCP23AA201 | CONDENSATE RETURN STORAGE TANK A OULET ISOLATION MOV | WATER | 25.987 | 65 | N/A | LCP4 | 650 | GB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 650 | A216-WCB | A351-CF8 | 150 | LUG | LATER | LATER
123 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | MOV | 20LCP24AA201 | CONDENSATE RETURN STORAGE TANK B OULET ISOLATION MOV | WATER | 25.987 | 65 | N/A | LCP4 | 650 | GB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 650 | A216-WCB | A351-CF8 | 150 | LUG | LATER | LATER
124 | 19K9-20LCP10-M05-0003 | CODENSATE SYEYEM - COMMON | CV | 20GHC40AA101 | DEMIN WATER MAKEUP FCV 1 | WATER | - | - | N/A | GHC4 | 150 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 150 | A351-CF8 | SS304 | 150 | BW | LATER | LATER
125 | 19K9-20LCP10-M05-0003 | CODENSATE SYEYEM - COMMON | CV | 20GHC40AA102 | DEMIN WATER MAKEUP FCV 2 | WATER | - | - | N/A | GHC4 | 150 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 150 | A351-CF8 | SS304 | 150 | BW | LATER | LATER
126 | 19K9-20LCP10-M05-0003 | CODENSATE SYEYEM - COMMON | PSV | 20LCP51AA191 | HEAT EXCHANGER CONDENSATE RETURN A TO CONDENSATE HEADER PSV | WATER | 25.987 | 110 | 26 | LCP7 | IN : 25 / OUT : 25 | LATER | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 25 | A105 | 316SS | 600 | RF | LATER | LATER
127 | 19K9-20LCP10-M05-0003 | CODENSATE SYEYEM - COMMON | PSV | 20LCP52AA191 | HEAT EXCHANGER CONDENSATE RETURN B TO CONDENSATE HEADER PSV | WATER | 25.987 | 110 | 26 | LCP7 | IN : 25 / OUT : 25 | LATER | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 25 | A105 | 316SS | 600 | RF | LATER | LATER
128 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | MOV | 20GHC60AA201 | DEMI WATER SYSTEM TO DEAERATOR & FEEDWATER STORAGE TANK A INLET MOV | WATER | - | - | N/A | GHC4 | 100 | HC1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 100 | A351-CF8 | SS304 | 150 | LATER | LATER | LATER
129 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | CV | 20LCA31AA101 | DEAERATOR & FEEDWATER STORAGE TANK A LCV | WATER | LATER | LATER | N/A | LCA8 | 500 | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 500 | LATER | LATER | LATER | LATER | LATER | LATER
130 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | CV | 20LBG11AA101 | DEAERATOR & FEEDWATER STORAGE TANK A PEGGING STEAM PCV | WATER | LATER | LATER | N/A | LBG1 | 80 | GB4 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
131 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | MOV | 20LBG11AA201 | DEAERATOR & FEEDWATER STORAGE TANK A PEGGING STEAM ISOLATION MOV | STEAM | LATER | LATER | N/A | LBG1 | 80 | GB4 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
132 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | CV | 20LAD01AA101 | DEAERATOR & FEEDWATER STORAGE TANK A HOT WATER INLET PCV | WATER | 40 | 185 | N/A | LAB7 | 150 | GB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 150 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
133 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | MOV | 20LAD01AA201 | DEAERATOR & FEEDWATER STORAGE TANK A HOT WATER INLET IOSLATION MOV | WATER | 40 | 185 | N/A | LAB7 | 150 | GB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
134 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | PSV | 20LAA01AA191 | DEAERATOR & FEEDWATER STORAGE TANK A PSV | STEAM | LATER | 205 | 10 | LAA1 | IN : 200 / OUT : 250 | LATER | SELF ACTUATING | ANGLE | N/A | N/A | IN : 200 / OUT : 250 | A105 | 316SS | 600 | RF | LATER | LATER
135 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | MOV | 20LAA01AA201 | DEAERATOR & FEEDWATER STORAGE TANK A VENT MOV | WATER | LATER | LATER | N/A | LAA1 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
136 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | MOV | 20LAB01AA201 | DEAERATOR & FEEDWATER STORAGE TANK A DRAIN MOV | WATER | 13 | 185 | N/A | LAB1 | 150 | HB3 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 150 | BW | LATER | LATER
137 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | MOV | 20LBR80AA201 | PENTANE EVAPORATOR TO DEAERATOR & FEEDWATER STORAGE TANK A INLET MOV | WATER | LATER | LATER | N/A | LBR10 | 50 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
138 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | MOV | 20GHC60AA202 | DEMI WATER SYSTEM TO DEAERATOR & FEEDWATER STORAGE TANK B INLET MOV | WATER | - | - | N/A | GHC4 | 100 | HC1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 100 | A351-CF8 | SS304 | 150 | LATER | LATER | LATER
139 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | CV | 20LCA32AA101 | DEAERATOR & FEEDWATER STORAGE TANK B LCV | WATER | LATER | LATER | N/A | LCA8 | 500 | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 500 | LATER | LATER | LATER | LATER | LATER | LATER
140 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | CV | 20LBG12AA101 | DEAERATOR & FEEDWATER STORAGE TANK B PEGGING STEAM PCV | WATER | LATER | LATER | N/A | LBG1 | 80 | GB4 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
141 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | MOV | 20LBG12AA201 | DEAERATOR & FEEDWATER STORAGE TANK B PEGGING STEAM ISOLATION MOV | STEAM | LATER | LATER | N/A | LBG1 | 80 | GB4 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
142 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | CV | 20LAD02AA101 | DEAERATOR & FEEDWATER STORAGE TANK B HOT WATER INLET PCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
143 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | MOV | 20LAD02AA201 | DEAERATOR & FEEDWATER STORAGE TANK B HOT WATER INLET IOSLATION MOV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
144 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | PSV | 20LAA02AA191 | DEAERATOR & FEEDWATER STORAGE TANK B PSV | STEAM | LATER | 205 | 10 | LAA1 | IN : 200 / OUT : 250 | LATER | SELF ACTUATING | ANGLE | N/A | N/A | IN : 200 / OUT : 250 | A105 | 316SS | 600 | RF | LATER | LATER
145 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | MOV | 20LAA02AA201 | DEAERATOR & FEEDWATER STORAGE TANK B VENT MOV | WATER | LATER | LATER | N/A | LAA1 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
146 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | MOV | 20LAB02AA201 | DEAERATOR & FEEDWATER STORAGE TANK B DRAIN MOV | WATER | 13 | 185 | N/A | LAB1 | 150 | HB3 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 150 | BW | LATER | LATER
147 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | MOV | 20LBR80AA202 | PENTANE EVAPORATOR TO DEAERATOR & FEEDWATER STORAGE TANK B INLET MOV | WATER | LATER | LATER | N/A | LBR10 | 50 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
148 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | MOV | 20GHC60AA203 | DEMI WATER SYSTEM TO DEAERATOR & FEEDWATER STORAGE TANK C INLET MOV | WATER | - | - | N/A | GHC4 | 100 | HC1 | MOTOR OPERATED (ON-OFF) | GLOBE | FAIL LOCK | CLASS IV | 100 | A351-CF8 | SS304 | 150 | LATER | LATER | LATER
149 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | CV | 20LCA33AA101 | DEAERATOR & FEEDWATER STORAGE TANK C LCV | WATER | LATER | LATER | N/A | LCA8 | 500 | LATER | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 500 | LATER | LATER | LATER | LATER | LATER | LATER
150 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | CV | 20LBG13AA101 | DEAERATOR & FEEDWATER STORAGE TANK C PEGGING STEAM PCV | WATER | LATER | LATER | N/A | LBG1 | 80 | GB4 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER
151 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | MOV | 20LBG13AA201 | DEAERATOR & FEEDWATER STORAGE TANK C PEGGING STEAM ISOLATION MOV | STEAM | LATER | LATER | N/A | LBG1 | 80 | GB4 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | A216-WCB | 13CR/STL | 300 | BW | LATER | LATER
152 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | CV | 20LAD03AA101 | DEAERATOR & FEEDWATER STORAGE TANK C HOT WATER INLET PCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
153 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | MOV | 20LAD03AA201 | DEAERATOR & FEEDWATER STORAGE TANK C HOT WATER INLET IOSLATION MOV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
154 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | PSV | 20LAA03AA191 | DEAERATOR & FEEDWATER STORAGE TANK C PSV | STEAM | LATER | 205 | 10 | LAA1 | IN : 200 / OUT : 250 | LATER | SELF ACTUATING | ANGLE | N/A | N/A | IN : 200 / OUT : 250 | A105 | 316SS | 600 | RF | LATER | LATER
155 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | MOV | 20LAA03AA201 | DEAERATOR & FEEDWATER STORAGE TANK C VENT MOV | WATER | LATER | LATER | N/A | LAA1 | 100 | LATER | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 100 | LATER | LATER | LATER | LATER | LATER | LATER
156 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | MOV | 20LAB03AA201 | DEAERATOR & FEEDWATER STORAGE TANK C DRAIN MOV | WATER | 13 | 185 | N/A | LAB1 | 150 | HB3 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 150 | BW | LATER | LATER
157 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | MOV | 20LBR80AA203 | PENTANE EVAPORATOR TO DEAERATOR & FEEDWATER STORAGE TANK C INLET MOV | WATER | LATER | LATER | N/A | LBR10 | 50 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
158 | 19K9-20LAB00-M05-0004 | FEEDWATER SYSTEM | MOV | 20LAB13AA201 | CONDENSATE PRE-HEAT EXCHANGER BYPASS MOV | WATER | 13 | 185 | N/A | LAB5 | 500 | HB3 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 500 | A216-WCB | 13CR/STL | 150 | BW | LATER | LATER
159 | 19K9-20LAB00-M05-0004 | FEEDWATER SYSTEM | PSV | 20LCA21AA191 | CONDENSATE PRE-HEAT EXCHANGER A TO DEAERATOR PSV | WATER | 25.987 | 110 | 26 | LCA7 | IN : 50 / OUT : 80 | GB2 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 50 / OUT : 80 | A105 | 316SS | 600 | RF | LATER | LATER
160 | 19K9-20LAB00-M05-0004 | FEEDWATER SYSTEM | PSV | 20LAB11AA191 | CONDENSATE PRE-HEAT EXCHANGER A TO COGEN FEEDWATER PUMP PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 50 / OUT : 80 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 50 / OUT : 80 | A105 | 316SS | 600 | RF | LATER | LATER
161 | 19K9-20LAB00-M05-0004 | FEEDWATER SYSTEM | PSV | 20LCA22AA191 | CONDENSATE PRE-HEAT EXCHANGER B TO DEAERATOR PSV | WATER | 25.987 | 110 | 26 | LCA7 | IN : 50 / OUT : 80 | GB2 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 50 / OUT : 80 | A105 | 316SS | 600 | RF | LATER | LATER
162 | 19K9-20LAB00-M05-0004 | FEEDWATER SYSTEM | PSV | 20LAB12AA191 | CONDENSATE PRE-HEAT EXCHANGER B TO COGEN FEEDWATER PUMP PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 50 / OUT : 80 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 50 / OUT : 80 | A105 | 316SS | 600 | RF | LATER | LATER
163 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | PSV | 20LAB31AA191 | COGEN FWP A SUCTION PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
164 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | MOV | 20LAB41AA201 | COGEN FWP A HHP DISCHARGE MOV | WATER | 197 | 185 | N/A | LAB6 | 300 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 300 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
165 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | CV | 20LAB41AA101 | COGEN FWP A MINIMUM RECIRCULATION FCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
166 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | PSV | 20LAB32AA191 | COGEN FWP B SUCTION PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
167 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | MOV | 20LAB42AA201 | COGEN FWP B HHP DISCHARGE MOV | WATER | 197 | 185 | N/A | LAB6 | 300 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 300 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
168 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | CV | 20LAB42AA101 | COGEN FWP B MINIMUM RECIRCULATION FCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
169 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | PSV | 20LAB33AA191 | COGEN FWP C SUCTION PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
170 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | MOV | 20LAB43AA201 | COGEN FWP C HHP DISCHARGE MOV | WATER | 197 | 185 | N/A | LAB6 | 300 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 300 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
171 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | CV | 20LAB43AA101 | COGEN FWP C MINIMUM RECIRCULATION FCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
172 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | PSV | 20LAB34AA191 | COGEN FWP D SUCTION PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
173 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | MOV | 20LAB44AA201 | COGEN FWP D HHP DISCHARGE MOV | WATER | 197 | 185 | N/A | LAB6 | 300 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 300 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
174 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | CV | 20LAB44AA101 | COGEN FWP D MINIMUM RECIRCULATION FCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
175 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | PSV | 20LAB35AA191 | COGEN FWP E SUCTION PSV | WATER | 13 | 185 | 13 | LAB5 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
176 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | MOV | 20LAB45AA201 | COGEN FWP E HHP DISCHARGE MOV | WATER | 197 | 185 | N/A | LAB6 | 300 | DB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 300 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
177 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | CV | 20LAB45AA101 | COGEN FWP E MINIMUM RECIRCULATION FCV | WATER | 197 | 185 | N/A | LAB6 | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 150 | A216-WCC | 13CR/STL | 1500 | BW | LATER | LATER
178 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | PSV | 25LAB11AA191 | TGP FWP A SUCTION PSV | WATER | 13 | 185 | 13 | LAB1 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
179 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | MOV | 25LAB21AA201 | TGP FWP A DISCHARGE MOV | WATER | 92.987 | 185 | N/A | LAB2 | 150 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
180 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB21AA101 | TGP FWP A MINIMUM RECIRCULATION FCV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
181 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | PSV | 25LAB12AA191 | TGP FWP B SUCTION PSV | WATER | 13 | 185 | 13 | LAB1 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
182 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | MOV | 25LAB22AA201 | TGP FWP B DISCHARGE MOV | WATER | 92.987 | 185 | N/A | LAB2 | 150 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
183 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB22AA101 | TGP FWP B MINIMUM RECIRCULATION FCV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
184 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | MOV | 25LAB41AA201 | TGP FWP DISCHARGE HEADER TO TGP ISOLATION MOV 1 | WATER | 92.987 | 185 | N/A | LAB2 | 250 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 250 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
185 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB41AA112 | TGP FWP DISCHARGE HEADER TO TGP PCV 1 | WATER | 92.987 | 185 | N/A | LAB2 | 250 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 250 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
186 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | MOV | 25LAB42AA201 | TGP FWP DISCHARGE HEADER TO TGP ISOLATION MOV 2 | WATER | 92.987 | 185 | N/A | LAB2 | 250 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 250 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
187 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB42AA112 | TGP FWP DISCHARGE HEADER TO TGP PCV 2 | WATER | 92.987 | 185 | N/A | LAB2 | 250 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 250 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
188 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | MOV | 25LAB43AA201 | TGP FWP DISCHARGE HEADER MOV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
189 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB43AA101 | TGP FWP DISCHARGE HEADER XV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GATE | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
190 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | PSV | 25LAB13AA191 | TGP FWP C SUCTION PSV | WATER | 13 | 185 | 13 | LAB1 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
191 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | MOV | 25LAB23AA201 | TGP FWP C DISCHARGE MOV | WATER | 92.987 | 185 | N/A | LAB2 | 150 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
192 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | CV | 25LAB23AA101 | TGP FWP C MINIMUM RECIRCULATION FCV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
193 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | PSV | 25LAB14AA191 | TGP FWP D SUCTION PSV | WATER | 13 | 185 | 13 | LAB1 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
194 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | MOV | 25LAB24AA201 | TGP FWP D DISCHARGE MOV | WATER | 92.987 | 185 | N/A | LAB2 | 150 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
195 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | CV | 25LAB24AA101 | TGP FWP D MINIMUM RECIRCULATION FCV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
196 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | PSV | 25LAB15AA191 | TGP FWP E SUCTION PSV | WATER | 13 | 185 | 13 | LAB1 | IN : 25 / OUT : 50 | HB3 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
197 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | MOV | 25LAB25AA201 | TGP FWP E DISCHARGE MOV | WATER | 92.987 | 185 | N/A | LAB2 | 150 | EB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 150 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
198 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | CV | 25LAB25AA101 | TGP FWP E MINIMUM RECIRCULATION FCV | WATER | 92.987 | 185 | N/A | LAB2 | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 80 | A216-WCB | 13CR/STL | 900 | BW | LATER | LATER
199 | 19K9-20PGB10-M05-0001 | CLOSED COOLING WATER SYSTEM | XV | 20GHC41AA251 | CCW EXPANSION HEAD TANK MAKEUP XV | WATER | LATER | LATER | N/A | GHC4 | 50 | HC1 | PNEUMATIC OPERATED (ON-OFF) | GATE | FAIL CLOSE | CLASS IV | 50 | A182-F304 | SS304 | 600 | SW | LATER | LATER
200 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 12PGB41AA191 | #12 ST GENERATOR COOLER CCW RETURN PSV 1 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
201 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 12PGB42AA191 | #12 ST GENERATOR COOLER CCW RETURN PSV 2 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
202 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 12PGB43AA191 | #12 ST GENERATOR COOLER CCW RETURN PSV 3 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
203 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 12PGB44AA191 | #12 ST GENERATOR COOLER CCW RETURN PSV 4 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
204 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 12PGB47AA191 | #12 ST LUBE OIL COOLER CCW RETURN PSV 1 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
205 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 12PGB48AA191 | #12 ST LUBE OIL COOLER CCW RETURN PSV 2 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
206 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 11PGB41AA191 | #11 ST GENERATOR COOLER CCW RETURN PSV 1 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
207 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 11PGB42AA191 | #11 ST GENERATOR COOLER CCW RETURN PSV 2 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
208 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 11PGB43AA191 | #11 ST GENERATOR COOLER CCW RETURN PSV 3 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
209 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 11PGB44AA191 | #11 ST GENERATOR COOLER CCW RETURN PSV 4 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
210 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 11PGB47AA191 | #11 ST LUBE OIL COOLER CCW RETURN PSV 1 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
211 | 19K9-20PGB10-M05-0004 | CLOSED COOLING WATER SYSTEM | PSV | 11PGB48AA191 | #11 ST LUBE OIL COOLER CCW RETURN PSV 2 | WATER | 11 | 70 | LATER | PGB1 | IN : 25 / OUT : 25 | HB4 | SELF ACTUATING | ANGLE | N/A | N/A | IN : 25 / OUT : 50 | A105 | 316SS | 600 | RF | LATER | LATER
212 | 19K9-20EGD00-M05-0001 | LIQUID PENTANE SUPPLY SYSTEM | XV | 20EGD00AA251 | LIQUID PENTANE INLET ISOLATION XV | LIQUID PENTANE | 18 | 70 | N/A | EGD1 | 150 | LATER | PNEUMATIC OPERATED (ON-OFF) | BALL | FAIL CLOSE | CLASS IV | 150 | LATER | LATER | LATER | LATER | LATER | LATER
213 | 19K9-20EGD00-M05-0001 | LIQUID PENTANE SUPPLY SYSTEM | XV | 20EKG70AA251 | PENTANE GAS OUTLET ISOLATION XV | PENTANE GAS | 18 | 150 | N/A | EKG10 | 350 | LATER | PNEUMATIC OPERATED (ON-OFF) | BALL | FAIL LOCK | CLASS IV | 350 | LATER | LATER | LATER | LATER | LATER | LATER
214 | 19K9-20EGD00-M05-0001 | LIQUID PENTANE SUPPLY SYSTEM | MOV | 20LBR16AA201 | PENTANE EVAPORATOR HP STEAM INLET MOV | STEAM | LATER | LATER | N/A | LBR1 | 80 | FB1 | MOTOR OPERATED (ON-OFF) | GATE | FAIL LOCK | CLASS IV | 80 | A216-WCB | 13CR/STL | 600 | BW | LATER | LATER
215 | 19K9-20EGD00-M05-0001 | LIQUID PENTANE SUPPLY SYSTEM | CV | 20LBR80AA101 | PENTANE GAS OUTLET TCV | STEAM | 50.3 | 399 | N/A | LBR10 | 50 | FB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | CLASS IV | 50 | A105 | 13CR/STL | 600 | SW | LATER | LATER
216 | 19K9-20GKB10-M05-0001 | POTABLE WATER DISTRIBUTION SYSTEM (COGEN) | MOV | 00GKB61AA201 | POTABLE/FIRE WATER RECEIVING TANK A NORMAL MAKE UP MOV | WATER | LATER | LATER | N/A | GKB6 | 450 | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 450 | A351-CF8 | A351-CF8 | 150 | LUG | LATER | LATER
217 | 19K9-20GKB10-M05-0001 | POTABLE WATER DISTRIBUTION SYSTEM (COGEN) | MOV | 00GKB61AA202 | POTABLE/FIRE WATER RECEIVING TANK B NORMAL MAKE UP MOV | WATER | LATER | LATER | N/A | GKB6 | 450 | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 450 | A351-CF8 | A351-CF8 | 150 | LUG | LATER | LATER
218 | 19K9-20GHC10-M05-0001 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | MOV | 20GHC01AA201 | DEMINERALIZED WATER STORAGE TANK A NORMAL MAKE UP MOV | WATER | 2 | 55 | N/A | GHC1 | 200 | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 200 | A351-CF8 | A351-CF8 | 150 | LUG | LATER | LATER
219 | 19K9-20GHC10-M05-0001 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | MOV | 20GHC02AA202 | DEMINERALIZED WATER STORAGE TANK B NORMAL MAKE UP MOV | WATER | 2 | 55 | N/A | GHC1 | 200 | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | CLASS IV | 200 | A351-CF8 | A351-CF8 | 150 | LUG | LATER | LATER
220 | 19K9-20GHC10-M05-0002 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | CV | 20GHC60AA101 | DEMINERALIZED WATER MAKE UP PUMP DISCHARGE TO DEAERATOR LCV | WATER | - | - | N/A | GHC4 | 100 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | CLASS IV | 100 | A351-CF8 | SS304 | 150 | BW | LATER | LATER
221 | 19K9-20GHC10-M05-0002 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | PSV | 20GHC30AA191 | CONDENSATE RETURN LINE PSV | WATER | LATER | LATER | LATER | GHC4 | LATER | HC1 | SELF ACTUATING | ANGLE | N/A | N/A | LATER | A182-F304 | SS304/STL | 600 | RF | LATER | LATER
222 | 19K9-20GHC10-M05-0002 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | PRV | 20GHC30AA701 | CONDENSATE RETURN LINE PRV | WATER | LATER | LATER | LATER | LATER | 150 | HC1 | SELF ACTUATING | GLOBE | N/A | N/A | 150 | A351-CF8 | SS304/STL | 150 | BW | LATER | LATER
223 | 19K9-20QFA10-M05-0001 | COMPRESSED AIR SYSTEM (COGEN) | XV | 20SCB01AA251 | COGEN SERVICE AIR HEADER ISOLATION XV | AIR | LATER | LATER | N/A | SCB1 | 80 | LATER | PNEUMATIC OPERATED (ON-OFF) | GATE | FAIL CLOSE | CLASS IV | 80 | LATER | LATER | LATER | LATER | LATER | LATER

## MOV
| NO. | Rev | STATUS | P/ID | SYSTEM | TYPE | KKS TAG | DESCRIPTION | FLUID | NORMAL OPERATING CONDITION |  |  | DESIGN CONDITION | [6 empty] | PDC | LINE SIZE | LINE MATERIAL | LINE SPEC (PMC) | SPECIFICATION | [12 empty] | VALVE |  | ACTUATOR |  |  | EXPLOSION PROOF | PIPE SCH. | Bore Size | Material | [5 empty] | Actuator Torque |  |  | Motor |  |  |  | Gear
[10 empty] | FLOW (M3/H) | PRESSURE INLET (BARG) | TEMP. (DEG.C) | FLOW (M3/H) | PRESSURE INLET (BARG) | TEMP. (DEG.C) | Specific Gravity (SG) | Viscosity (Cp) | VAPOUR PRESSURE, Pv (Bara) | Max. Shutoff Pressure (D/P) |  |  |  |  | ACTUATOR TYPE | BODY TYPE | FAIL POSITION | TRAVEL TIME | LEAKAGE CLASS | SIZE (DN) | BODY MATERIAL | TRIM MATERIAL | INTERNAL COATING | VALVE RATING | END CONNECTION | DISC/PLUG TYPE | BONNET TYPE | MAKER | MODEL NO. | MAKER | MODEL NO. | TYPE |  |  |  | Disc | Seat | Stem | Packing | Gasket | Bonnet | Required Torque | Seleted Torque | Set Torque | MAKER | MODEL NO. | Rated Power | Time Rating | MAKER | MODEL NO. | Ratio
SCT Design Data | 5 |  |  | 1A5J-00PGB10-M05-0001 | CLOSED COOLING WATER SYSTEM | MOV | 00PGB21AA201 | FIN-FAN TYPE COOLER A DISCHARGE HEADER MOV | WATER | 1850 | 6 | 48.8 | 1850 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 550 | A53-B | HB2 | MOTOR OPERATED (INCHING) | BUTTERFLY | FAIL LOCK | <50sec | API 598 | 550 | A216-WCB | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | STD
| 6 |  |  | 1A5J-00PGB10-M05-0001 | CLOSED COOLING WATER SYSTEM | MOV | 00PGB22AA201 | FIN-FAN TYPE COOLER B DISCHARGE HEADER MOV | WATER | 1850 | 6 | 48.8 | 1850 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 550 | A53-B | HB2 | MOTOR OPERATED (INCHING) | BUTTERFLY | FAIL LOCK | <50sec | API 598 | 550 | A216-WCB | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | STD
| 7 |  |  | 1A5J-00PGB10-M05-0002 | CLOSED COOLING WATER SYSTEM | MOV | 11PGB20AA201 | GT #11 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | <40sec | API 598 | 400 | A216-WCB | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | STD
| 8 |  |  | 1A5J-00PGB10-M05-0002 | CLOSED COOLING WATER SYSTEM | MOV | 12PGB20AA201 | GT #12 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | <40sec | API 598 | 400 | A216-WCB | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | STD
| 9 |  |  | 1A5J-00PGB10-M05-0003 | CLOSED COOLING WATER SYSTEM | MOV | 13PGB20AA201 | GT #13 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | <40sec | API 598 | 400 | A216-WCB | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | STD
| 10 |  |  | 1A5J-00PGB10-M05-0003 | CLOSED COOLING WATER SYSTEM | MOV | 14PGB20AA201 | GT #14 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | <40sec | API 598 | 400 | A216-WCB | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | STD
| 11 |  |  | 1A5J-00GHB10-M05-0001 | SERVICE WATER DIST, SYSTEM | MOV | 00GHB01AA201 | SERVICE AND FIRE WATER STORAGE TANK A INLET MOV | WATER | 300 | 2 | AMB | 300 | 3.5 | 60 | 0.9872 | 0.5 | 0.136 | 3.5 | GHB1 | 200 | A312-TP304L | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | <20sec | API 598 | 200 | A351-CF3 | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | 10S
| 12 |  |  | 1A5J-00GHB10-M05-0001 | SERVICE WATER DIST, SYSTEM | MOV | 00GHB02AA201 | SERVICE AND FIRE WATER STORAGE TANK B INLET MOV | WATER | 300 | 2 | AMB | 300 | 3.5 | 60 | 0.9872 | 0.5 | 0.136 | 3.5 | GHB1 | 200 | A312-TP304L | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | <20sec | API 598 | 200 | A351-CF3 | A351-CF8 |  | 150 | LUG | Concentric | BB |  |  |  |  | Multi. or Quarter Turn | N/A | 10S
| 5 |  |  | 1A5J-00PGB10-M05-0001 | CLOSED COOLING WATER SYSTEM | MOV | 00PGB21AA201 | FIN-FAN TYPE COOLER A DISCHARGE HEADER MOV | WATER | 1850 | 6 | 48.8 | 1850 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 550 | A53-B | HB2 | MOTOR OPERATED (INCHING) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 6 |  |  | 1A5J-00PGB10-M05-0001 | CLOSED COOLING WATER SYSTEM | MOV | 00PGB22AA201 | FIN-FAN TYPE COOLER B DISCHARGE HEADER MOV | WATER | 1850 | 6 | 48.8 | 1850 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 550 | A53-B | HB2 | MOTOR OPERATED (INCHING) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 7 |  |  | 1A5J-00PGB10-M05-0002 | CLOSED COOLING WATER SYSTEM | MOV | 11PGB20AA201 | GT #11 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 8 |  |  | 1A5J-00PGB10-M05-0002 | CLOSED COOLING WATER SYSTEM | MOV | 12PGB20AA201 | GT #12 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 9 |  |  | 1A5J-00PGB10-M05-0003 | CLOSED COOLING WATER SYSTEM | MOV | 13PGB20AA201 | GT #13 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 10 |  |  | 1A5J-00PGB10-M05-0003 | CLOSED COOLING WATER SYSTEM | MOV | 14PGB20AA201 | GT #14 CCW SUPPLY MOV | WATER | 925 | 6 | 48.8 | 925 | 9 | 70 | 0.9888 | 0.5 | 0.1163 | 9 | PGB2 | 400 | A53-B | HB2 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 11 |  |  | 1A5J-00GHB10-M05-0001 | SERVICE WATER DIST, SYSTEM | MOV | 00GHB01AA201 | SERVICE AND FIRE WATER STORAGE TANK A INLET MOV | WATER | 300 | 2 | AMB | 300 | 3.5 | 60 | 0.9872 | 0.5 | 0.136 | 3.5 | GHB1 | 200 | A312-TP304L | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 12 |  |  | 1A5J-00GHB10-M05-0001 | SERVICE WATER DIST, SYSTEM | MOV | 00GHB02AA201 | SERVICE AND FIRE WATER STORAGE TANK B INLET MOV | WATER | 300 | 2 | AMB | 300 | 3.5 | 60 | 0.9872 | 0.5 | 0.136 | 3.5 | GHB1 | 200 | A312-TP304L | HC1 | MOTOR OPERATED (ON-OFF) | BUTTERFLY | FAIL LOCK | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 17 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 18 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 19 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 20 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 21 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 22 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 23 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 24 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 25 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 26 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 27 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 28 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 29 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 30 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 31 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 32 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 33 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 34 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 35 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 36 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 37 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 38 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 39 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 40 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 41 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 42 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 43 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
| 44 | [25 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * |  | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
Vendor to fill-up on '*' marked cell without any blank.

## SDT_220118 (hidden)
No. | Description | PDC | Operating condition |  |  |  | Design condition |  |  |  | PMC (Material) | Pipe | Pipe | Pipe | Min. Req. Wall THK'N | Velocity Criteria | P&ID No. | Piping Specification
|  |  | Mass Flow | Press. | Press. | Temp. | Mass Flow | Press. | Press. | Temp. |  | Material | NB | Sch. |  |  |  | Mat'l Group | Flange Rating | Class No. |  |  |  | Corrosion Allowace (mm) | Req. Th'k | Selected Th'k |  | Valves
|  |  | kg/s | [bara] | [barg] | deg.C | kg/s | [bara] | [barg] | deg.C |  | ASTM | mm |  |  | m/s |  |  |  |  | Rating | Mat'l | Sequence |  | (mm) | Sch | Th'k (mm) | Body | Trim | Bonnet | Stream Number | Date | Time | Rev
A | Steam System
1 | Each AB Outlet to HHP HDR 21/22A | LBA1 | 94.4 | 140 | 138.987 | 567.1 | 94.4 | 148.013 | 147 | 574 | BA1 | SA335P91 | 250 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 20.03 | SCH120 | 21.44 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
2 | HHP STM Header 21/22A | LBA2 | 188.8 | 140 | 138.987 | 567.1 | 188.8 | 148.013 | 147 | 574 | BA2 | A335P91 | 400 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 29.81 | SCH120 | 30.96 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
3 | Each HRSG Outlet to HHP HDR 21/22B | LBA1 | 160.5 | 140 | 138.987 | 567.1 | 160.5 | 148.013 | 147 | 574 | BA1 | SA335P91 | 350 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 37.26 | SCH120 | 38.1 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
4 | HHP STM Header 21/22B | LBA2 | 351.4 | 140 | 138.987 | 567.1 | 351.4 | 148.013 | 147 | 574 | BA2 | A335P91 | 500 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 20.03 | SCH120 | 21.44 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
5 | HHP STM Header 21/22B to ST HHP Inlet | LBA2 | 183.8 | 140 | 138.987 | 567.1 | 183.8 | 148.013 | 147 | 574 | BA2 | A335P91 | 400 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 29.81 | SCH120 | 30.96 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
6 | HHP to HP Letdown VV Inlet | LBA2 | 21.7698 | 140 | 138.987 | 567.1 | 21.7698 | 148.013 | 147 | 574 | BA2 | A335P91 | 100 | 120 |  | 100 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 37.26 | SCH120 | 38.1 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
7 | HHP to LP Letdown VV Inlet | LBA2 | 267.5735 | 140 | 138.987 | 567.1 | 267.5735 | 148.013 | 147 | 574 | BA2 | A335P91 | 400 | 140 |  | 100 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 26.08 | SCH120 | 27.79 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
8 | Each HRSG/AB Start Up Bypass Inlet | LBA2 | 46.8 | 108.72 | 107.707 | 567.1 | 46.8 | 148.013 | 147 | 574 | BA2 | A335P91 | 200 | 140 |  | 100 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 29.81 | SCH120 | 30.96 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
9 | ST Start Up Bypass Inlet | LBA2 | 35.1 | 127.8 | 126.787 | 563.7 | 35.1 | 148.013 | 147 | 574 | BA2 | A335P91 | 200 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 12.35 | SCH120 | 14.27 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
10 | ST Start Up Bypass Outlet | LBA2 | 40.2886 | 80 | 78.987 | 390 | 40.2886 | 148.013 | 147 | 574 | BA2 | A335P91 | 200 | 140 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 12.35 | SCH120 | 14.27 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
11 | HHP ST Bypass to ACC Inlet | LBA2 | 40.2886 | 140 | 138.987 | 567.1 | 40.2886 | 148.013 | 147 | 574 | BA2 | A335P91 | 200 | 140 |  | 100 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 12.35 | SCH120 | 14.27 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
12 | HHP Steam Drain Valve Outlet | LBA10 | - | - | - | - | - | 148.013 | 147 | 574 | BA2 | A335P91 | 40 | 80 |  | - |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 12.35 | SCH120 | 14.27 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
13 | HP STM HEADER | LBR1 | 85 | 47.2078 | 46.1948 | 371.1111 | 85 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 450 | 60 |  | 70 |  | 1.15 | 2500 | BA1 | B | A | 1 | 0 | 16.07 | SCH120 | 18.26 | A217-C12A | 17CR/STL | PSB OS&Y |  | 2019-05-17 | 14:03
14 | HP STM HDR to TGP | LBR1 | 85 | 47.2078 | 46.1948 | 371.1111 | 85 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 750 | Special | 25.7424 | - |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 3.33 | SCH40 | 6.02 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
15 | HP STM HDR to Each HP ST Nozzle | LBR1 | 42.5 | 47.2078 | 46.1948 | 371.1111 | 42.5 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 250 | 60 |  | 70 |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 4.9 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
16 | HP STM HDR to TGP Warmup | LBR1 | 0 | 47.2078 | 46.1948 | 371.1111 | 0 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 50 | 80 |  | - |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 4.9 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
17 | Aux Steam Letdown VV Inlet | LBR1 | 3.7086 | 47.2078 | 46.1948 | 371.1111 | 3.7086 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 80 | 80 |  | 70 |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 6.38 | SCH30 | 7.04 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
18 | HHP to HP Letdown VV Outlet | LBR1 | 25.2 | 47.2078 | 46.1948 | 371.1111 | 25.2 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 150 | 80 |  | 100 |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 7.95 | SCH40 | 9.27 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
19 | HP-LP Letdown Valve Inlet | LBR1 | 85 | 47.2078 | 46.1948 | 371.1111 | 85 | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 300 | 60 |  | 100 |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 7.95 | SCH40 | 9.27 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
20 | HP Steam Drain Valve Outlet | LBR10 | - | - | - | - | - | 51.3446 | 50.3 | 399 | FB1 | A106Gr.B | 40 | 80 |  | - |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 6.38 | SCH30 | 7.04 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
21 | Each HRSG Outlet to LP HDR | LBA3 | 5.799 | 9.6314 | 8.6184 | 247.1 | 5.799 | 10.6656 | 9.7 | 253 | HB1 | SA106Gr.B | 200 | 40 |  | 60 |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 7.95 | SCH40 | 9.27 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
22 | LP STM Header | NAA1 | 341.5 | 9.6314 | 8.6184 | 247.1 | 341.5 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 1300 | Special | 9.53 | 60 |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 2.59 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
23 | LP STM Header to TGP T.P. | NAA1 | 341.5 | 9.6314 | 8.6184 | 247.1 | 341.5 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 1500 | Special | 8.9351 | - |  | 1.1 | 600 | FB1 | F | B | 1 | 0 | 2.59 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
24 | LP STM HDR to TGP Warmup | NAA1 | 0 | 9.6314 | 8.6184 | 247.1 | 0 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 50 | 80 |  | - |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 4.26 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
25 | ST HP Ext to Ext Letdown Valve | LBD1 | 169.3 | 9.6314 | 8.6184 | 247.1 | 169.3 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 1000 | STD |  | 60 |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 8.85 | 9.53 | 9.53 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
26 | ST Ext Letdown Valve to LP Header | LBD2 | 171.0404 | 9.6314 | 8.6184 | 247.1 | 171.0404 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 1000 | STD |  | 60 |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 8.85 | 9.53 | 9.53 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
27 | HP-LP Letdown Valve Outlet | NAA1 | 94.2555 | 9.6314 | 8.6184 | 247.1 | 94.2555 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 600 | STD |  | 100 |  | 1.1 | 300 | GB1 | G | B | 1 | 1.6 | 6.81 | SCH10 | 7.92 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
28 | LP Bypass to ACC Inlet | NAA1 | 71.35 | 9.6314 | 8.6184 | 247.1 | 71.35 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 600 | STD |  | 100 |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 6.42 | SCH10 | 7.92 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
29 | HHP to LP Letdown VV Outlet | NAA1 | 341.5 | 9.6314 | 8.6184 | 247.1 | 341.5 | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 1100 | STD |  | 100 |  | 1.1 | 300 | GB1 | G | B | 1 | 1.6 | 2.8 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
30 | LP Steam Drain Valve Outlet | NAA10 | - | - | - | - | - | 10.6656 | 9.7 | 253 | HB2 | A106Gr.B | 50 | 80 |  | - |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 6.15 | SCH10 | 7.92 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
31 | HHP ST Bypass to ACC Outlet | LBA8 | 48.0939 | 3.2 | 2.187 | 135.74 | 48.0939 | 8.013 | 7 | 170 | HB3 | A106Gr.B | 800 | STD |  | 100 |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 8.31 | STD | 9.53 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
32 | LP Bypass to ACC Outlet | LBA8 | 77.128 | 3.2 | 2.187 | 135.74 | 77.128 | 8.013 | 7 | 170 | HB3 | A106Gr.B | 900 | STD |  | 100 |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 7.77 | STD | 9.53 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
33 | HRSG/BLR HHP Startup Bypass Outlet | LBA8 | 63.9041 | 3.2 | 2.187 | 135.74 | 63.9041 | 8.013 | 7 | 170 | HB3 | A106Gr.B | 800 | STD |  | 100 |  | 1.1 | 150 | HB1 | H | B | 1 | 1.6 | 5.34 | SCH10 | 7.92 | A216-WCB | 13CR/STL | BB OS&Y |  | 2019-05-17 | 14:03
34 | Aux STM Letdown Valve Outlet | LBG1 | 3.7086 | 11 | 9.987 | 322.3796 | 3.7086 | 12.013 | 12 | 330 | GB4 | A106Gr.B | 150 | 40 |  | 60 |  | #N/A | 150 | #N/A | H | #N/A | 1 | 1.6 | 5.07 | SCH5 | 5.54 | #N/A | #N/A | BB OS&Y |  | 2019-05-17 | 14:03
35 | Aux STM ST Gland Seal Steam | LBG1 | 1.3889 | 11 | 9.987 | 322.3796 | 1.3889 | 12.013 | 12 | 330 | GB4 | A106Gr.B | 100 | 40 |  | 60 |  | #N/A | 150 | #N/A | H | #N/A | 1 | 1.6 | 2.73 | SCH40 | 7.11 | #N/A | #N/A | BB OS&Y |  | 2019-05-17 | 14:03
36 | Aux STM ACC Motive Steam | LBG1 | 1.2222 | 11 | 9.987 | 322.3796 | 1.2222 | 12.013 | 12 | 330 | GB4 | A106Gr.B | 100 | 40 |  | 60
37 | Aux STM DEA Backup Steam Header | LBG1 | 2.7258 | 11 | 9.987 | 322.3796 | 2.7258 | 12.013 | 12 | 330 | GB4 | A106Gr.B | 150 | 40 |  | 60
38 | Aux STM DEA Backup Steam Branch | LBG1 | 0.90861 | 11 | 9.987 | 322.3796 | 0.90861 | 12.013 | 12 | 330 | GB4 | A106Gr.B | 80 | 40 |  | 60
B | Feed Water System
| TGP Feedwater System | [16 empty] | 김종민 선임
Suction
| TGP Feedwater Deaerator Outlet (individual) | LAB1 | 85.25 | 4.013 | 3 | 107.8 | 86 | 11.987 | 13 | 185 | HB3 | A106Gr.B | 300 | STD |  | 3 |  | 김종민 선임
| TGP FWP Suction, HDR | LAB1 | 170.5 | 4.013 | 3 | 107.8 | 171 | 11.987 | 13 | 185 | HB3 | A106Gr.B | 300 | STD |  | 3 |  | 김종민 선임
| TGP FWP Suction, individual | LAB1 | 49.22 | 4.013 | 3 | 107.8 | 50 | 11.987 | 13 | 185 | HB3 | A106Gr.B | 150 | 40 |  | 3 |  | 김종민 선임
Discharge
| TGP FWP Discharge, individual | LAB2 | 49.22 | 75.4 | 74.387 | 108.3 | 50 | 94 | 92.987 | 185 | EB1 | A106Gr.B | 150 | 40 |  | 5 |  | 김종민 선임
| TGP FWP Discharge, HDR and each Line to Reducer | LAB2 | 170.5 | 75.4 | 74.387 | 108.3 | 171 | 94 | 92.987 | 185 | EB1 | A106Gr.B | 250 | 40 |  | 5 |  | 김종민 선임
| TGP FWP Discharge, HDR from Reducer | LAB2 | 170.5 | 75.4 | 74.387 | 108.3 | 171 | 94 | 92.987 | 185 | EB1 | A106Gr.B | 400 | 40 |  | 2.25 |  | 김종민 선임
| TGP FWP Minimum Recirculation upstream PCV, Individual | LAB2 | 14.766 | 75.4 | 74.387 | 108.3 | 15 | 94 | 92.987 | 185 | EB1 | A106Gr.B | 80 | 40 |  | 5 |  | 김종민 선임
| TGP FWP Minimum Recirculation downstream PCV, Individual | LAB3 | 14.766 | 8 | 6.987 | 108.3 | 15 | 10 | 8.987 | 185 | HB3 | A106Gr.B | 80 | 40 |  | 5 |  | 김종민 선임
| TGP FWP Minimum Recirculation, HDR | LAB3 | 14.766 | 8 | 6.987 | 108.3 | 15 | 10 | 8.987 | 185 | HB3 | A106Gr.B | 100 | 40 |  | 5 |  | 김종민 선임
| TGP FWP Minimum Recirculation, to each Deaerator | LAB3 | 7.383 | 8 | 6.987 | 108.3 | 8 | 10 | 8.987 | 185 | HB3 | A106Gr.B | 80 | 40 |  | 5 |  | 김종민 선임
Cogen Feedwater System
Suction
| Cogen Feedwater Deaerator Outlet (individual) | LAB1 | 251.98 | 3.513 | 2.5 | 107.8 | 252 | 14.013 | 13 | 185 | HB3 | A106Gr.B | 500 | STD |  | 3 |  | 김종민 선임
| Cogen Feedwater Deaerator Outlet Header to CPHX | LAB1 | 503.96 | 3.513 | 2.5 | 107.8 | 504 | 14.013 | 13 | 185 | HB3 | A106Gr.B | 500 | STD |  | 3 |  | 김종민 선임
| CPHX to Cogen FWP Suction Header | LAB5 | 503.96 | 3.513 | 2.5 | 94.1 | 504 | 14.013 | 13 | 185 | HB3 | A106Gr.B | 500 | 40 |  | 3 |  | 김종민 선임
| Cogen FWP Suction, Individual | LAB5 | 167.9867 | 3.513 | 2.5 | 94.1 | 168 | 14.013 | 13 | 185 | HB3 | A106Gr.B | 300 | 40 |  | 3
Discharge - HHP
| Cogen FWP HHP Dishcarge, Individual | LAB6 | 124.3611 | 161.613 | 160.6 | 94.1 | 125 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 300 | 160 |  | 3 |  | 김종민 선임
| Cogen FWP HHP Discharge Header | LAB6 | 373.0833 | 161.613 | 160.6 | 94.1 | 374 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 500 | 160 |  | 5 |  | 김종민 선임
| HHP Desuperheating Water Supply Header | LAB6 | 13.5 | 161.613 | 160.6 | 94.1 | 14 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 100 | 160 |  | 5 |  | 김종민 선임
| HHP Desuperheating Water for HHP Letdown to HP | LAB6 | 5.7 | 161.613 | 160.6 | 94.1 | 6 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 80 | 160 |  | 5 |  | 김종민 선임
| HHP Desuperheating Water for ST Cold Start-up bypass V/V | LAB6 | 7.8 | 161.613 | 160.6 | 94.1 | 8 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 80 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply Header for HRSGs and ABs | LAB6 | 359.5833 | 161.613 | 160.6 | 94.1 | 360 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 450 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply Header to HRSG #14, 15 | LAB6 | 251.9722 | 161.613 | 160.6 | 94.1 | 252 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 350 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply to HRSG #14, 15, Individual | LAB6 | 125.9861 | 161.613 | 160.6 | 94.1 | 126 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 300 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply Header to HRSG #13, Aux Boiler | LAB6 | 314.6972 | 161.613 | 160.6 | 94.1 | 315 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 400 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply to Aux. Boiler Header | LAB6 | 188.7111 | 161.613 | 160.6 | 94.1 | 189 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 300 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply to Aux. Boiler Individual | LAB6 | 94.3556 | 161.613 | 160.6 | 94.1 | 95 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 200 | 160 |  | 5 |  | 김종민 선임
| HHP Feedwater Supply to HRSG #13 | LAB6 | 125.9861 | 161.613 | 160.6 | 94.1 | 126 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 300 | 160 |  | 5 |  | 김종민 선임
Discharge - LP
| Cogen FWP LP Discharge, Individual | LAB7 | 41.23 | 35.513 | 34.5 | 94.1 | 42 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 150 | 40 |  | 5 |  | 김종민 선임
| Cogen FWP LP Discharge Header | LAB7 | 123.69 | 35.513 | 34.5 | 94.1 | 124 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 250 | 40 |  | 5 |  | 김종민 선임
| LP Desuperheating Water Supply Header | LAB7 | 83.44 | 35.513 | 34.5 | 94.1 | 84 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 200 | 40 |  | 5 |  | 김종민 선임
| LP Desuperheating Water for HHP Letdown to LP | LAB7 | 73.2 | 35.513 | 34.5 | 94.1 | 74 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 200 | 40 |  | 5 |  | 김종민 선임
| LP Desuperheating Water for HP Letdown to LP | LAB7 | 7.7 | 35.513 | 34.5 | 94.1 | 8 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 80 | 80 |  | 5 |  | 김종민 선임
| LP Desuperheating Water for TBN Extraction Attemperator Header | LAB7 | 2.5 | 35.513 | 34.5 | 94.1 | 3 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 50 | 80 |  | 5 |  | 김종민 선임
| LP Desuperheating Water for TBN Extraction Attemperator | LAB7 | 0.04 | 35.513 | 34.5 | 94.1 | 1 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 25 | 160 |  | 5 |  | 김종민 선임
| LP Feedwater Supply Header for HRSGs | LAB7 | 40.25 | 35.513 | 34.5 | 94.1 | 41 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 150 | 80 |  | 5 |  | 김종민 선임
| LP Feedwater Supply Header to HRSG #14, #15 | LAB7 | 26.8333 | 35.513 | 34.5 | 94.1 | 27 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 150 | 80 |  | 5
| LP Feedwater Supply to HRSG #14, #15, Individual | LAB7 | 13.4167 | 35.513 | 34.5 | 94.1 | 14 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 100 | 80 |  | 5
| LP Feedwater Supply to HRSG #13 | LAB7 | 13.4167 | 35.513 | 34.5 | 94.1 | 14 | 41.013 | 40 | 185 | GB1 | A106Gr.B | 100 | 80 |  | 5 |  | 김종민 선임
| Cogen FWP Minimum Recirculation upstream PCV, Individual | LAB6 | 37.3083 | 161.613 | 160.6 | 94.1 | 38 | 198.013 | 197 | 185 | DB1 | A106Gr.C | 150 | 160 |  | 5 |  | 김종민 선임
| Cogen FWP Minimum Recirculation downstream PCV, Individual | LAB8 | 37.3083 | 1.3 | 0.287 | 94.1 | 38 | 11.013 | 10 | 185 | HB3 | A106Gr.B | 150 | 40 |  | 5 |  | 김종민 선임
| Cogen FWP Minimum Recirculation, HDR | LAB8 | 74.6167 | 1.3 | 0.287 | 94.1 | 75 | 11.013 | 10 | 185 | HB3 | A106Gr.B | 200 | 40 |  | 5 |  | 김종민 선임
| Cogen FWP Minimum Recirculation, to each Deaerator | LAB8 | 37.3083 | 1.3 | 0.287 | 94.1 | 38 | 11.013 | 10 | 185 | HB3 | A106Gr.B | 150 | 40 |  | 5 |  | 김종민 선임
김종민 선임
C | Condensate Extraction System (ACC to DEA)
Main line
1 | CEP Suction line (Individual) | LCA1 | 43 | 12.3 | 11.287 | 93.5 | 43 | 19 | 18 & FV | 100 | GB2 | A106Gr.B | 200 | 40 |  | 1.5
2 | CEP Discharge line (Individual) | LCA2 | 43 | 12.3 | 11.287 | 93.5 | 43 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 150 | 40 |  | 3
3 | CEP Discharge line (Condensate header, Unit) | LCA2 | 120 | 12.3 | 11.287 | 93.5 | 120 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 250 | 40 |  | 3
4 | CEP Discharge line (Condensate header, Two(2) units) | LCA2 | 233.6 | 12.3 | 11.287 | 93.5 | 233.6 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 350 | STD |  | 3
5 | CEP Discharge line (After Return condensate & FG performance heater junction) | LCP6 | 515.6 | 12.3 | 11.287 | 101 | 515.6 | 27 | 25.987 | 110 | GB2 | A106Gr.B | 500 | STD |  | 3
6 | Deaerator inlet line (Individual) | LCA7 | 515.6 | 12.3 | 11.287 | 105 | 515.6 | 27 | 25.987 | 110 | GB2 | A106Gr.B | 500 | STD |  | 3
Miscellaneous line
1 | CEP Minimum recirculation line | LCA2 | 23 | 12.3 | 11.287 | 93.5 | 23 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 100 | 40 |  | 3
2 | Condensate dump line | LCA2 | 8.9 | 12.3 | 11.287 | 93.5 | 8.9 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 80 | 40 |  | 3
3-1 | ACC consumer header | LCA2 | 1.1 | 12.3 | 11.287 | 93.5 | 1.1 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 50 | 40 |  | 3
3-2 |  | LCW1 | 1.1 | 4 | 2.987 | 93.5 | 1.1 | 4.2 | 4 | 100 | HB3 | A106Gr.B | 50 | 40 |  | 3
4 | Flash tank spray water | LCW1 | 1 | 4 | 2.987 | 93.5 | 1 | 4.2 | 4 | 100 | HB3 | A106Gr.B | 50 | 40 |  | 3
5 | Seal water to Vacuum breaker | LCW1 | 0.02 | 4 | 2.987 | 93.5 | 0.02 | 4.2 | 4 | 100 | HB3 | A106Gr.B | 25 | 40 |  | 3
6-1 | ST consumer header | LCA2 | 2.2 | 12.3 | 11.287 | 93.5 | 2.4 | 19 | 17.987 | 100 | GB2 | A106Gr.B | 50 | 40 |  | 3
6-2 |  | LCW2 | 2.2 | 4 | 2.987 | 93.5 | 2.4 | 4.2 | 5.5 | 100 | HB3 | A106Gr.B | 50 | 40 |  | 3
7 | Turbine exhaust hood spray water | LCW2 | 2 | 4 | 2.987 | 93.5 | 2 | 4.2 | 5.5 | 100 | HB3 | A106Gr.B | 50 | 40 |  | 3
8 | Seal steam cooler spray water | LCW2 | 0.2 | 4 | 2.987 | 93.5 | 0.2 | 4.2 | 5.5 | 100 | HB3 | A106Gr.B | 15 | 40 |  | 3
9 | From Oxygen scavenger dosing | LCA2 | - | 12.3 | 11.287 | 93.5 | - | 19 | 17 | 100 | GB2 | A106Gr.B | 25 | 40 |  | 3
10 | From Ammonia dosing | LCA2 | - | 12.3 | 11.287 | 93.5 | - | 19 | 17 | 100 | GB2 | A106Gr.B | 25 | 40 |  | 3
11 | Demin water initial filling line | LCA2 | - | 12.3 | 11.287 | 93.5 | - | 19 | 17.987 | 100 | GB2 | A106Gr.B | 80 | 40 |  | 3
12 | To Sampling cooler | LCA2 | - | 12.3 | 11.287 | 93.5 | - | 19 | 17 | 100 | GB2 | A106Gr.B | 25 | 40 |  | 3
D | Condensate Return System (TGP to DEA)
Main line
1-1 | From TGP TP (Apply to TGP TP Velocity limitation and TP Size) | LCP1 | 376.5 | 6.1 | 5.087 | 121.1 | 419.4 | 15.5 | 14.5 & F.V | 148.9 | HB3 | A106Gr.B | 600 | STD |  | 2.25
1-2 | From TGP TP (Apply to Cogen velocity limitation) to CR HX | LCP1 | 376.5 | 6.1 | 5.087 | 121.1 | 419.4 | 15.5 | 14.5 & F.V | 148.9 | HB3 | A106Gr.B | 450 | STD |  | 3
2 | From CR HX (Hot side) to Condensate return storage tank | LCP2 | 376.5 | 6.1 | 5.087 | 57 | 419.4 | 15.5 | 14.5 & F.V | 65 | HB3 | A106Gr.B | 450 | STD |  | 3
3 | From Condensate return storage tank to Condensate supply pump | LCP3 | 376.5 | 3 | 1.987 | 57 | 376.5 | 4 | 2.987 | 65 | HB3 | A106Gr.B | 650 | STD |  | 1.5
4 | From Condensate supply pump to Fin-Fan cooler | LCP4 | 376.5 | 20.7 | 19.687 | 57 | 376.5 | 27 | 25.987 | 65 | GB2 | A106Gr.B | 450 | STD |  | 3
5 | From Fin-Fan cooler to Makeup junction | LCP5 | 376.5 | 20.7 | 19.687 | 54 | 376.5 | 27 | 25.987 | 60 | GB2 | A106Gr.B | 450 | STD |  | 3
6 | From Makeup junction to CR HX (Cold side) | LCP5 | 400.9 | 20.7 | 19.687 | 54 | 400.9 | 27 | 25.987 | 60 | GB2 | A106Gr.B | 450 | STD |  | 3
7 | From CR HX (Cold side) to Condensate header | LCP6 | 400.9 | 20.7 | 19.687 | 102.4 | 400.9 | 27 | 25.987 | 110 | GB2 | A106Gr.B | 450 | STD |  | 3
Miscellaneous line
1 | CSP Minimum recirculation line | LCP4 | 94.2 | 19.8 | 18.787 | 57 | 98.8 | 27 | 25.987 | 65 | GB2 | A106Gr.B | 250 | 40 |  | 3
2 | Demin water makeup line | GHC4 | 39.9 | - | - | - | 39.9 | - | - | - | HC1 | A312TP304 | 150 | 40 |  | 3
3 | From Oxygen scavenger dosing | LCP5 | - | 19.8 | 18.787 | 54 | - | 27 | 17 | 60 | GB2 | A106Gr.B | 25 | 40 |  | 3
4 | From Ammonia dosing | LCP5 | - | 19.8 | 18.787 | 54 | - | 27 | 17 | 60 | GB2 | A106Gr.B | 25 | 40 |  | 3
5 | To Sampling cooler | LCP5 | - | 19.8 | 18.787 | 54 | - | 27 | 25.987 | 60 | GB2 | A106Gr.B | 25 | 40 |  | 3
E | Fuel gas supply System
1 | Fuel Gas Supply From TGP | EKG1 | 39.838 | 56.1711 | 55.1581 | 54.4444 | 39.838 | 87.8869 | 86.8739 | 87.7778 | FB2 | A106Gr.B | 300 | Sch80 | 15.076 | 25
2 | Start-up Gas Supply From TGP | EKG1 |  | 68.5816 | 67.5686 | 60 |  | 87.8869 | 86.8739 | 87.7778 | FB2 | A106Gr.B | 350 | Sch80 | 16.3725 | 25 |  | 25 | 23.9362 | FB3 | F | B | 3 | 1.6 | 17.27 | SCH80 | 21.44 | A216-WCB | 13CR/STL | BB OS&Y
3 | Fuel Gas Supply Header to Each PRV Branch | EKG1 | 13.2793 | 56.1711 | 55.1581 | 54.4444 | 13.2793 | 87.8869 | 86.8739 | 87.7778 | FB2 | A106Gr.B | 200 | Sch80 | 10.7897 | 25 |  | 25 | 1.2449 | FB3 | F | B | 3 | 1.6 | 10.16 | SCH60 | 10.31 | A216-WCB | 13CR/STL | BB OS&Y
4 | Fuel Gas Supply Header to a Start-up PRV Branch | EKG1 | 0.23 | 56.1711 | 55.1581 | 54.4444 | 0.23 | 87.8869 | 86.8739 | 87.7778 | FB2 | A106Gr.B | 80 | Sch40 | 4.1615 | 25 |  | 25 | 18.5088 | FB3 | F | B | 3 | 1.6 | 17.27 | SCH80 | 21.44 | A216-WCB | 13CR/STL | BB OS&Y
5 | Each PRV Branch Outlet to PRV Station Outlet Header | EKG2 | 13.2793 | 35.413 | 34.4 | 54.4444 | 13.2793 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 200 | Sch40 | 5.8642 | 25 |  | 25 | 1.2449 | FB3 | F | B | 3 | 1.6 | 12.21 | SCH60 | 12.7 | A216-WCB | 13CR/STL | BB OS&Y
6 | Start-up PRV Branch Outlet to PRV Station Outlet Header | EKG2 | 0.23 | 35.413 | 34.4 | 54.4444 | 0.23 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 80 | Sch40 | 3.2937 | 25 |  | 25 | 18.3827 | GC2 | G | C | 2 | 1.6 | 7.8 | SCH30 | 8.38 | A351-CF8 | SS304/STL | BB OS&Y
7 | PRV Station Outlet to Fuel Gas Main Supply Header #1 | EKG2 | 39.838 | 35.413 | 34.4 | 54.4444 | 39.838 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 350 | Sch40 | 8.3785 | 25 |  | 25 | 1.9463 | FC1 | F | C | 1 | 0 | 7.7 | SCH40S | 9.53 | A351-CF8 | SS304/STL | BB OS&Y
8 | Fuel Gas Main Supply Header #1 to GT#13 Branch | EKG2 | 37.28 | 35.413 | 34.4 | 54.4444 | 37.28 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 350 | Sch40 | 8.3785 | 25 |  | 25 | 20.4328 | FB4 | F | B | 4 | 1.6 | 3.81 | SCH80 | 5.54 | #N/A | #N/A | BB OS&Y
9 | GT Branch to GT Coalescing Filter Inlet | EKG3 | 12.44 | 35.413 | 34.4 | 54.4444 | 12.44 | 39.513 | 38.5 | 60 | GC2 | A312TP304 | 200 | Sch40 | 5.5269 | 25 |  | 25 | Sch40 | FB4 | F | B | 4 | 1.6 | 3.81 | SCH80 | 5.54 | #N/A | #N/A | BB OS&Y
10 | Each GT Coalescing Filter Outlet to Each GT Performance Heater Inlet | EKG3 | 12.44 | 35.413 | 34.4 | 54.4444 | 12.44 | 39.513 | 38.5 | 60 | GC2 | A312TP304 | 200 | Sch40 | 5.5269 | 25 |  | 25 | 17.4526 | EB1 | E | B | 1 | 1.6 | 4.59 | SCH80 | 5.54 | #N/A | #N/A | PSB OS&Y
11 | Each GT Performance Heater Outlet to Each GT inlet (FG1) | EKG4 | 12.44 | 35.413 | 34.4 | 227.417 | 12.44 | 39.513 | 38.5 | 235 | FC1 | A312TP304 | 250 | Sch40 | 8.27 | 25 |  | 25 | 17.4526 | DC1 | D | C | 1 | 0 | 5.41 | SCH80S | 5.54 | #N/A | #N/A | PSB OS&Y
12 | Fuel Gas Main Supply Header #2 to GT#14 Branch | EKG2 | 24.88 | 35.413 | 34.4 | 54.4444 | 24.88 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 250 | Sch40 | 6.8589 | 25 |  | 25 | 18.7389 | DC1 | D | C | 1 | 0 | 5.41 | SCH80S | 5.54 | #N/A | #N/A | PSB OS&Y
13 | Fuel Gas Main Supply Header #3 to GT#15 Branch | EKG2 | 12.44 | 35.413 | 34.4 | 54.4444 | 12.44 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 200 | Sch40 | 6.8589 | 25 |  | 25 | 22.1121 | FB3 | F | B | 3 | 1.6 | 12.21 | SCH60 | 12.7 | A216-WCB | 13CR/STL | BB OS&Y
14 | Fuel Gas Main Supply Header to Aux. PRV Station Inlet Header | EKG2 | 13.9 | 35.413 | 34.4 | 54.4444 | 13.9 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 200 | Sch40 | 5.8642 | 25 |  | 25 | 22.1121 | FB1 | F | B | 1 | 0 | 4.9 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y
15 | Aux PRV Station Inlet Header to Each Aux. PRV Inlet Branch | EKG2 | 6.95 | 35.413 | 34.4 | 54.4444 | 6.95 | 39.513 | 38.5 | 60 | GB3 | A106Gr.B | 200 | Sch40 | 4.9285 | 25 |  | 25 | 19.2748
16 | Each Aux. PRV Outlet Branch to Aux. PRV Station Outlet Header #1 | EKG5 | 6.95 | 16.013 | 15 | 54.4444 | 6.95 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 150 | Sch40 | 3.6235 | 25 |  | 25 | 16.7374
17 | Aux. Consumer Header #1 to Aux. Boiler #16 Branch | EKG5 | 13.9 | 16.013 | 15 | 54.4444 | 13.9 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 300 | Sch40 | 4.482 | 25 |  | 25 | 21.0956
18 | Each Aux. Boiler Branch to Aux. Boiler Inlet | EKG5 | 6.5 | 16.013 | 15 | 54.4444 | 6.5 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 200 | Sch40 | 3.6235 | 25 |  | 25 | 18.911
19 | Aux. Consumer Header #2 to Aux. Boiler #17 Branch | EKG5 | 7.4 | 16.013 | 15 | 54.4444 | 7.4 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 200 | Sch40 | 4.482 | 25 |  | 25 | 19.9678
20 | Aux. Consumer Header #3 to HRSG #13 DB Branch | EKG5 | 2.638 | 16.013 | 15 | 54.4444 | 2.638 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 150 | Sch40 | 4.482 | 25 |  | 25 | 22.7326
21 | Each HRSG DB Branch to HRSG Duct Burner Unit | EKG5 | 0.9 | 16.013 | 15 | 54.4444 | 0.9 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 80 | Sch40 | 2.5569 | 25 |  | 25 | 13.8784
22 | Aux. Consumer Header #4 to HRSG #14 DB Branch | EKG5 | 1.738 | 16.013 | 15 | 54.4444 | 1.738 | 18.013 | 17 | 60 | HB3 | A106Gr.B | 100 | Sch40 | 4.482 | 25 |  | 25 | 18.2795
23 | Fuel Gas Vent Line (Before Performance Heater) | EKG6 | 0 | 1.013 | 0 | 54.4444 | 0 | 4.513 | 3.5 | 60 | HB3 | A106Gr.B | 25 | Sch80 |  | 25 |  | 25 | 20.9871
24 | Fuel Gas Vent Line (After Performance Heater) | EKG7 | 0 | 1.013 | 0 | 227.417 | 0 | 4.513 | 3.5 | 235 | HB3 | A106Gr.B | 25 | Sch80 |  | 25 |  | 25
25 | Fuel Gas Performance Heater Supply | LAB20 | 7.17 | 144.4 | 143.387 | 252.5 | 7.17 | 198 | 196.987 | 339 | BB1 | A106Gr.B | 80 | Sch160 |  | 5 |  | 25
26 | Fuel Gas Performance Heater Return | LCA20 | 7.17 | 19 | 17.987 | 61 | 7.17 | 27 | 25.987 | 110 | GB2 | A106Gr.B | 80 | Sch40 |  | 3 |  | 25
F | Compressed Air System | [16 empty] | 25
1 | Instrument Air Header (Cogen) | QFB1 | 909 Nm3/h | 9.1 | 9.1 | 50 | 1445 Nm3/h | 11 | 11 | 60 | HC2 | A312-T304L | 80 | STD |  | 30 | 19K9-20QFA10-M05-0001_RA |  | 150 | HC1 | H | C | 1 | 0 | 0.73 | SCH5S | 2.11 | A351-CF8 | SS304/STL | BB OS&Y
2 | Service Air Header (Cogen) | QFB2 | 76 Nm3/h | 9.1 | 9.1 | 50 | 109 Nm3/h | 11 | 11 | 60 | HC2 | A312-T304L | 80 | STD |  | 30 | 19K9-20QFA10-M05-0001_RA |  | 150 | #N/A | H | #N/A | 1 | 0 | 0.73 | SCH5S | 2.11 | #N/A | #N/A | BB OS&Y
3 | Instrument Air Header (Desal) | QFB1 | 112 Nm3/h | 9.1 | 9.1 | 50 | 240 Nm3/h | 11 | 11 | 60 | HC2 | A312-T304L | 50 | STD |  | 30 | 19K9-50QFA10-M05-0001_RA
4 | Service Air Header (Desal) | QFB2 | 32 Nm3/h | 9.1 | 9.1 | 50 | 46 Nm3/h | 11 | 11 | 60 | HC2 | A312-T304L | 25 | STD |  | 30 | 19K9-50QFA10-M05-0001_RA
19K9-00QJA10-M05-0002 Service gas system (2 of 2)
H | Waste Water Transfer System for Cogen Area (incl. Sanitary) | [16 empty] | 19K9-00QJA10-M05-0002 Service gas system (2 of 2)
1 | Waste Water Drain Inlet from GT-HRSG Area | GMB1 | Later | 1.013 | 0 | 100 | Later | 2.013 | 1 | 120 | CPVC | CPVC | Later | Later |  |  |  | 19K9-00QJA10-M05-0002 Service gas system (2 of 2)
2 | Waste Water Drain Inlet from Other Area | GMB2 | Later | 1.013 | 0 | 37 | Later | 2.013 | 1 | 45 | CPVC | CPVC | Later | Later |  |  |  | 19K9-00QJA10-M05-0002 Service gas system (2 of 2)
3 | HRSG#13 BD TANK PIT CHEMICAL WASTE WATER LIFT STATION | GMB3 | 2.21 | 5.013 | 4 | 100 | 2.873 | 6.013 | 5 | 120 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMB10-M05-0001 | 19K9-00QJA10-M05-0002 Service gas system (2 of 2)
4 | GT#13 EVACOOLER DRAIN CHEMICAL WASTE WATER LIFT STATION | GMB4 | 6.9 | 5.013 | 4 | 37 | 8.97 | 6.013 | 5 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMB10-M05-0001 |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | A105 | 13CR/STL | BB OS&Y
5 | HRSG#14 BD TANK PIT CHEMICAL WASTE WATER LIFT STATION | GMB3 | 2.21 | 5.013 | 4 | 100 | 2.873 | 6.013 | 5 | 120 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMB10-M05-0001 |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.21 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
6 | GT#14 EVACOOLER DRAIN CHEMICAL WASTE WATER LIFT STATION | GMB4 | 6.9 | 5.013 | 4 | 37 | 8.97 | 6.013 | 5 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMB10-M05-0001 |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | A105 | 13CR/STL | BB OS&Y
7 | HRSG#15 BD TANK PIT CHEMICAL WASTE WATER LIFT STATION | GMB3 | 2.21 | 5.013 | 4 | 100 | 2.873 | 6.013 | 5 | 120 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMB10-M05-0001 |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.21 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
8 | GT#15 EVACOOLER DRAIN CHEMICAL WASTE WATER LIFT STATION | GMB4 | 6.9 | 5.013 | 4 | 37 | 8.97 | 6.013 | 5 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | #N/A | #N/A | BB OS&Y
9 | ST#11 CLEAN DRAIN TANK PIT CHEMICAL WASTE WATER LIFT STATION | GMB3 | 1.38 | 5.013 | 4 | 100 | 1.794 | 6.013 | 5 | 120 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.21 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
10 | ST#12 CLEAN DRAIN TANK PIT CHEMICAL WASTE WATER LIFT STATION | GMB3 | 1.38 | 5.013 | 4 | 100 | 1.794 | 6.013 | 5 | 120 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.14 | SCH80 | 5.54 | A105 | 13CR/STL | BB OS&Y
11 | AUX. BOILER#16, 17 BD Tank PIT CHEMICAL WASTE WATER LIFT STATION | GMB3 | 3.31 | 5.013 | 4 | 100 | 4.303 | 6.013 | 5 | 120 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.14 | SCH80 | 5.54 | A105 | 13CR/STL | BB OS&Y
12 | ACC AREA CHEMICAL WASTE WATER LIFT STATION | GMB4 | 1.93 | 5.013 | 4 | 37 | 2.509 | 6.013 | 5 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | A105 | 13CR/STL | BB OS&Y
13 | Oily Waste Water Drain Inlet | GMA1 | Later | 1.013 | 0 | 37 | Later | 2.013 | 1 | 45 | Later | Later | Later | Later |  | Later |  | 1.1
14 | GT#13 AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMA10-M05-0002 | 1.1
15 | GT#14 AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1
16 | GT#15 AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMB10-M05-0001 | 1.1
17 | GT#13 TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 10.21 | 7.013 | 6 | 37 | 13.273 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMA10-M05-0002
18 | GT#14 TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 10.21 | 7.013 | 6 | 37 | 13.273 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMB10-M05-0001
19 | GT#15 TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 10.21 | 7.013 | 6 | 37 | 13.273 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMB10-M05-0001
20 | ST#11 AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.4 | 7.013 | 6 | 37 | 1.82 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMB10-M05-0001
21 | ST#12 AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.4 | 7.013 | 6 | 37 | 1.82 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 25 | STD |  | 3 | 198L-00GMA10-M05-0001
22 | ST#11 TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 9.11 | 7.013 | 6 | 37 | 11.843 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMA10-M05-0001
23 | FEEDWATER PUMP AREA OILY WASTE WATER LIFT STATION | GMA2 | 8.83 | 7.013 | 6 | 37 | 11.479 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMA10-M05-0002
24 | ST#12 TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 9.11 | 7.013 | 6 | 37 | 11.843 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 80 | STD |  | 3 | 198L-00GMA10-M05-0001 |  | 150 | HL2 | H | L | 2 | 0 | SDR11 | SDR11 | -
25 | AUX. BOILER #16 & 17 AREA OILY WASTE WATER LIFT STATION | GMA2 | 4.69 | 7.013 | 6 | 37 | 6.097 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 |  | 150 | HL2 | H | L | 2 | 0 | SDR11 | SDR11 | -
26 | AUX. BOILER TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.4 | 7.013 | 6 | 37 | 1.82 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 |  | 150 | HL2 | H | L | 2 | 0 | SDR11 | SDR11 | -
27 | ACC TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.93 | 7.013 | 6 | 37 | 2.509 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 |  | 150 | HL2 | H | L | 2 | 0 | SDR11 | SDR11 | -
28 | WORKSHOP AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 | HDPE
29 | EDG AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 | HDPE
30 | FIRE PUMP HOUSE AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 | HDPE
31 | WT/WWT TRANSFORMER AREA OILY WASTE WATER LIFT STATION | GMA2 | 1.38 | 7.013 | 6 | 37 | 1.794 | 8.013 | 7 | 45 | HB3 | A106Gr.B | 50 | STD |  | 3 | 198L-00GMA10-M05-0002 | HDPE | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | A105 | 13CR/STL | BB OS&Y
32 | Sanitary Sewer Inlet | GQA1 | Later | 1.013 | 0 | 37 | Later | 2.013 | 1 | 45 | UPVC | UPVC | Later | Later |  |  |  |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.21 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
33 | CCR BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | A105 | 13CR/STL | BB OS&Y
34 | WORKSHOP & STORE BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 |  | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.21 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
35 | SOCIAL & ADMINISTRATION BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | #N/A | #N/A | BB OS&Y
36 | HIGH SECURITY BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.21 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
37 | SECURITY CONTROL CENTER SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.14 | SCH80 | 5.54 | A105 | 13CR/STL | BB OS&Y
38 | WT/WWT BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.14 | SCH80 | 5.54 | A105 | 13CR/STL | BB OS&Y
[18 empty] | 1.1 | 150 | HB5 (Galv) | H | B | 5 (Galv) | 0 | 0.11 | SCH80 | 5.08 | A105 | 13CR/STL | BB OS&Y
35 | SOCIAL & ADMINISTRATION BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1
36 | HIGH SECURITY BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1
37 | SECURITY CONTROL CENTER SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1 | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
38 | WT/WWT BUILDING SANITARY SEWER LIFT STATION | GQA2 | 1.38 | 6.013 | 5 | 37 | 1.794 | 7.013 | 6 | 45 | HDPE | HDPE | 50 | SDR11 |  | 3 | 198L-00GQA10-M05-0001 | 1.1 | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
[19 empty] | 150 | HC1 | 0 | 1.75 | SCH5S | 3.4 | A351-CF8 | SS304/STL | BB OS&Y
I | Potable Water System (Cogen) | [17 empty] | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
1 | Desal plant to potable water receiving tank |  | 150.4167 | 9.813 | 8.8 | 37 | 150.4167 | 12.513 | 11.5 | 40 | A312TP304 | A312TP304 | 450 | STD |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 1.75 | SCH5S | 3.4 | A351-CF8 | SS304/STL | BB OS&Y
2 | Potable water receiving tank to Potable water transfer pumps (to TGP)_Common | GKB1 | 333 | 2.713 | 1.7 | 37 | 333 | 3.053 | 2.04 | 40 | HC1 | A312TP304 | 300 | STD |  | 1.5 |  | 2.1
3 | Potable water transfer pumps (to TGP) suction | GKB1 | 167 | 2.713 | 1.7 | 37 | 167 | 3.053 | 2.04 | 40 | HC1 | A312TP304 | 200 | STD |  | 1.5 |  | 2.1 | 150 | HC1 | 0 | 2.07 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
4 | Potable water transfer pumps (to TGP) discharge | GKB2 | 167 | 9.613 | 8.6 | 37 | 167 | 13.013 | 12 | 40 | HC1 | A312TP304 | 200 | STD |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
5 | Potable water transfer pumps (to TGP) header (AG) | GKB2 | 333 | 9.613 | 8.6 | 37 | 333 | 13.013 | 12 | 40 | HC1 | A312TP304 | 200 | STD |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
6 | Potable water transfer pumps (to TGP) header T.P | GKB2 | 333 | 9.613 | 8.6 | 37 | 333 | 13.013 | 12 | 40 | HC1 | A312TP304 | 300 |  |  | 2.25 |  |  | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
7 | Potable water receiving tank to Potable water transfer pumps (to Demin Plant)_Common | GKB1 | 140.5556 | 2.713 | 1.7 | 37 | 140.5556 | 3.053 | 2.04 | 40 | HC1 | A312TP304 | 300 | STD |  | 1.5 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
8 | Potable water transfer pumps (to Demin Plant) suction | GBK1 | 79 | 2.713 | 1.7 | 37 | 79 | 3.053 | 2.04 | 40 | A312TP304 | A312TP304 | 150 | STD |  | 1.5 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
9 | Potable water transfer pumps (to Demin Plant) discharge | GBK3 | 79 | 7.513 | 6.5 | 50 | 79 | 10.013 | 9 | 55 | A312TP304 | A312TP304 | 150 | STD |  | 3 |  | 2.1 | 150 | HC1 | 0 | 0.73 | SCH5S | 2.11 | A351-CF8 | SS304/STL | BB OS&Y
10 | Potable water transfer pumps (to Demin Plant) header (AG) | GBK3 | 121 | 7.513 | 6.5 | 50 | 121 | 10.013 | 9 | 55 | A312TP304 | A312TP304 | 200 | STD |  | 3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
11 | Potable water transfer pumps (to Cogen) suction | GBK1 | 35 | 2.713 | 1.7 | 37 | 35 | 3.053 | 2.04 | 50 | A312TP304 | A312TP304 | 200 | STD |  | 1.5 |  | 2.1
12 | Potable water transfer pumps (to Cogen) discharge | GKB4 | 35 | 10.513 | 9.5 | 37 | 35 | 14.013 | 13 | 50 | HC1 | A312TP304 | 150 | STD |  | 3 |  | 2.1
13 | Potable water transfer pumps (to Cogen) header (AG) | GKB4 | 81 | 10.513 | 9.5 | 37 | 81 | 14.013 | 13 | 50 | HC1 | A312TP304 | 200 | STD |  | 3 |  | 2.1 | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
J | Service Water System (Cogen) | [17 empty] | 150 | HC1 | 0 | 0.39 | SCH40S | 3.91 | A182-F304 | SS304/STL | BB OS&Y
1 | Service Water System (Cogen) | GHA1 | 66.6667 | 10.513 | 9.5 | 37 | 66.6667 | 14.013 | 13 | 55 | HC1 | A312TP304 | 200 | STD |  | 3 |  | 2.1 | 150 | HC1 | 0 | 0.39 | SCH40S | 3.91 | A182-F304 | SS304/STL | BB OS&Y
[19 empty] | 150 | HC1 | 0 | 0.39 | SCH40S | 3.91 | A182-F304 | SS304/STL | BB OS&Y
K | Demineralized Water System (Cogen) | [17 empty] | 150 | HC1 | 0 | 0.39 | SCH40S | 3.91 | A182-F304 | SS304/STL | BB OS&Y
1 | Demin plant to demineralized water storage tank |  | LATER |  | LATER | 37 | LATER |  | LATER | 55 | A312TP304 | A312TP304 | [5 empty] | 2.1 | 150 | HC1 | 0 | 0.57 | SCH5S | 2.11 | A351-CF8 | SS304/STL | BB OS&Y
2 | Demineralized Water Storage Tank to Demin water transfer pumps (to TGP) | GHC1 | 58.3333 | 2.513 | 1.5 | 37 | 58.3333 | 3.013 | 2 | 55 | HC1 | A312TP304 | 250 | STD |  | 1.5 |  | 2.1 | 150 | HL1 | 0 | 0.39 | SCH40S | 3.91 | #N/A | #N/A | BB OS&Y
3 | Demin water transfer pumps (to TGP) suction | GHC1 | 2.1111 | 2.513 | 1.5 | 37 | 2.1111 | 3.013 | 2 | 55 | HC1 | A312TP304 | 50 | STD |  | 1.5 |  | 2.1 | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
4 | Demin water transfer pumps (to TGP) discharge | GHC2 | 2.7778 | 10.413 | 9.4 | 37 | 2.7778 | 14.013 | 13 | 55 | HC1 | A312TP304 | 50 | STD |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
5 | Demin water transfer pumps (to TGP) header (AG) | GHC2 | 2.7778 | 10.413 | 9.4 | 37 | 2.7778 | 14.013 | 13 | 55 | HC1 | A312TP304 | 80 | STD |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 0.73 | SCH5S | 2.11 | A351-CF8 | SS304/STL | BB OS&Y
6 | Demin water transfer pumps (to TGP) header T.P | GHC2 | 2.7778 | 10.413 | 9.4 | 37 | 2.7778 | 14.013 | 13 | 55 | HC1 | A312TP304 | 100 | STD |  | 2.25 |  | HDPE | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
7 | Demin water make-up pumps suction | GHC1 | 25 | 2.513 | 1.5 | 37 | 25 | 3.013 | 2 | 55 | HC1 | A312TP304 | 150 | STD |  | 1.5 |  | 2.1
8 | Demin water make-up pumps discharge | GHC3 | 25 | 16.313 | 15.3 | 37 | 25 | 21.013 | 20 | 55 | GC1 | A312TP304 | 150 | STD |  | 3 |  | 2.1
9 | Demin water make-up pumps header (AG) | GHC3 | 50 | 16.313 | 15.3 | 37 | 50 | 21.013 | 20 | 55 | GC1 | A312TP304 | 150 | STD |  | 3 |  | 2.1 | 150 | HB1 | H | B | 1 | 1.6 | 3 | SCH20 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
[19 empty] | 150 | HB1 | H | B | 1 | 1.6 | 2.09 | SCH80 | 5.08 | #N/A | #N/A | BB OS&Y
L | Liquid Pentane System | [17 empty] | 150 | HB1 | H | B | 1 | 1.6 | 2.09 | SCH80 | 5.08 | #N/A | #N/A | BB OS&Y
1 | TGP TP to Pentane Evaporator | EGD1 | 18 | 6.5 | 5.5 | 60.6 | 18.002 | 6.825 | 18 | 70 |  | A106Gr.B | 150 | STD |  | H | 2.25 | 19K9-20EDG00-M05-0001_RA
2 | Pentane Evaporator to KO Drum | EKG11 | 18.002 | 5.5 | 4.5 | 100 | 18.002 | 5.775 | 18 | 150 | GB5 | A106Gr.B | 350 | STD |  | H | 2.25 | 19K9-20EDG00-M05-0001_RA
3 | KO Drum to Main Header | EKG10 | 18.002 | 4.9 | 3.9 | 99 | 18.002 | 5.145 | 18 | 150 | GB5 | A106Gr.B | 350 | STD |  | H | 20 | 19K9-20EDG00-M05-0001_RA
4 | HP Steam from HP Steam Header | LBR1 | 3.3889 | 47.2 | 46.2 | 371 | 3.6111 | 52 | 50.3 | 399 | FB1 | A106Gr.B | 80 | 60 |  | H | 60 | 19K9-20EDG00-M05-0001_RA | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
5 | Pentane Evaporator to Deaerator | LBR10 | 3.3889 | 43.7 | 42.7 | 243 | 3.6111 | 52 | 50.3 | 399 | FB1 | A106Gr.B | 50 | 60 |  | H | 3 | 19K9-20EDG00-M05-0001_RA | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
[19 empty] | 150 | HB4 | H | B | 4 | 1.6 | 3.31 | SCH20 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
M | Closed Cooling System | [17 empty] | 150 | HB4 | H | B | 4 | 1.6 | 2.97 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y
1 | Common CCW pump suction header PGB00BR001 | PGB1 | 3083.3722 | 11.0466 | 10.0336 | 60.2967 | 3237.5408 | 12.013 | 11 | 70 | HB4 | A53-B | 650 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A216-WCB | 13CR/STL | BB OS&Y
2 | CCW pump Suction | PGB1 | 1541.6861 | 11.0466 | 10.0336 | 60.2967 | 1618.7704 | 12.013 | 11 | 70 | HB4 | A53-B | 500 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A105 | 13CR/STL | BB OS&Y
3 | CCW pump Discharge | PGB1 | 1541.6861 | 11.0466 | 10.0336 | 60.2967 | 1618.7704 | 12.013 | 11 | 70 | HB4 | A53-B | 500 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A216-WCB | 13CR/STL | BB OS&Y
4 | Common CCW pump discharge header PGB10BR001 | PGB1 | 3083.3722 | 11.0466 | 10.0336 | 60.2967 | 3237.5408 | 12.013 | 11 | 70 | HB4 | A53-B | 650 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
5 | Common FFC supply header PGB20BR001 | PGB2 | 3075.0906 | 11.0466 | 10.0336 | 55 | 3228.8451 | 12.013 | 11 | 70 | HB4 | A53-B | 650 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
6 | QMS header supply | PGB2 | 25.5586 | 11.0466 | 10.0336 | 55 | 26.8365 | 12.013 | 11 | 70 | HB4 | A53-B | 80 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A105 | 13CR/STL | BB OS&Y
7 | QMS for Cogen supply | PGB2 | 15.5318 | 11.0466 | 10.0336 | 55 | 16.3083 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 1.98 | SCH80 | 3.73 | A216-WCB | 13CR/STL | BB OS&Y
8 | QMS for TGP supply | PGB2 | 10.0268 | 11.0466 | 10.0336 | 55 | 10.5282 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.43 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
9 | SWAS for Aux. Boiler supply | PGB2 | 20.8401 | 11.0466 | 10.0336 | 55 | 21.8821 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
10 | Air compressor cooler supply | PGB2 | 103.414 | 11.0466 | 10.0336 | 55 | 108.5847 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A105 | 13CR/STL | BB OS&Y
11 | #13 GT header supply | PGB2 | 504.2905 | 11.0466 | 10.0336 | 55 | 529.505 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1
12 | SWAS for #13HRSG supply | PGB2 | 23.4942 | 11.0466 | 10.0336 | 55 | 24.6689 | 12.013 | 11 | 70 | HB4 | A53-B | 80 | 40 |  | 3 |  | 1.1
13 | GT Generator Cooler supply | PGB2 | 468.9017 | 11.0466 | 10.0336 | 55 | 492.3468 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1
14 | #13 GT sub header1 supply | PGB2 | 11.8946 | 11.0466 | 10.0336 | 55 | 12.4893 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1
15 | GT Gas Dryer Cooler supply | PGB2 | 0.68812 | 11.0466 | 10.0336 | 55 | 0.72252 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 25 | 80 |  | 3
16 | GT LCI Cooler supply | PGB2 | 11.2065 | 11.0466 | 10.0336 | 55 | 11.7668 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3
17 | GT Lube Oil Cooler supply | PGB2 | 223.1461 | 11.0466 | 10.0336 | 55 | 234.3034 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3
18 | GT Lube Oil Cooler Bypass | PGB2 | 281.1444 | 11.0466 | 10.0336 | 55 | 295.2016 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3
19 | Common CCW supply header PGB20BR002 | PGB2 | 2420.9875 | 11.0466 | 10.0336 | 55 | 2542.0369 | 12.013 | 11 | 70 | HB4 | A53-B | 600 | STD |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
20 | #Cogen & TGP BFP supply | PGB2 | 109.1155 | 11.0466 | 10.0336 | 55 | 114.5713 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
21 | COGEN FWP Supply Header | PGB2 | 84.5399 | 11.0466 | 10.0336 | 55 | 88.7669 | 12.013 | 11 | 70 | HB4 | A53-B | 100 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 3.31 | SCH20 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
22 | COGEN FWP Supply Branch | PGB2 | 16.908 | 11.0466 | 10.0336 | 55 | 17.7534 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 2.97 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y
23 | TGP FWP Supply Header | PGB2 | 24.5756 | 11.0466 | 10.0336 | 55 | 25.8043 | 12.013 | 11 | 70 | HB4 | A53-B | 80 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A216-WCB | 13CR/STL | BB OS&Y
24 | TGP FWP Supply Branch | PGB2 | 4.9151 | 11.0466 | 10.0336 | 55 | 5.1609 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A105 | 13CR/STL | BB OS&Y
25 | Min recirculation Line | PGB2 | 56.3557 | 11.0466 | 10.0336 | 55 | 59.1735 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A216-WCB | 13CR/STL | BB OS&Y
26 | #11 ST header supply | PGB2 | 659.608 | 11.0466 | 10.0336 | 55 | 692.5884 | 12.013 | 11 | 70 | HB4 | A53-B | 300 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
27 | ST Generator Cooler Supply Header | PGB2 | 511.1716 | 11.0466 | 10.0336 | 55 | 536.7302 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
28 | ST Generator Cooler Supply Branch | PGB2 | 127.7929 | 11.0466 | 10.0336 | 55 | 134.1826 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A105 | 13CR/STL | BB OS&Y
29 | #11 ST sub header1 supply | PGB2 | 148.4364 | 11.0466 | 10.0336 | 55 | 155.8582 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 1.98 | SCH80 | 3.73 | A216-WCB | 13CR/STL | BB OS&Y
30 | ST Lube Oil Cooler Supply Header | PGB2 | 142.5382 | 11.0466 | 10.0336 | 55 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.43 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
31 | ST Lube Oil Cooler Supply Branch | PGB2 | 142.5382 | 11.0466 | 10.0336 | 55 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
32 | ST Hydraulic Unit Cooler supply | PGB2 | 5.8981 | 11.0466 | 10.0336 | 55 | 6.193 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A105 | 13CR/STL | BB OS&Y
33 | Common CCW supply header PGB20BR003 | PGB2 | 1652.264 | 11.0466 | 10.0336 | 55 | 1734.8772 | 12.013 | 11 | 70 | HB4 | A53-B | 500 | STD |  | 3 |  | 1.1
34 | #12 ST header supply | PGB2 | 659.608 | 11.0466 | 10.0336 | 55 | 692.5884 | 12.013 | 11 | 70 | HB4 | A53-B | 300 | STD |  | 3 |  | 1.1
35 | ST Generator Cooler Supply Header | PGB2 | 511.1716 | 11.0466 | 10.0336 | 55 | 536.7302 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1
36 | ST Generator Cooler Supply Branch | PGB2 | 127.7929 | 11.0466 | 10.0336 | 55 | 134.1826 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1
37 | #12 ST sub header1 supply | PGB2 | 148.4364 | 11.0466 | 10.0336 | 55 | 155.8582 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3
38 | ST Lube Oil Cooler Supply Header | PGB2 | 142.5382 | 11.0466 | 10.0336 | 55 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3
39 | ST Lube Oil Cooler Supply Branch | PGB2 | 142.5382 | 11.0466 | 10.0336 | 55 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3
40 | ST Hydraulic Unit Cooler supply | PGB2 | 5.8981 | 11.0466 | 10.0336 | 55 | 6.193 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3
41 | Common CCW supply header PGB20BR004 | PGB2 | 992.656 | 11.0466 | 10.0336 | 55 | 1042.2888 | 12.013 | 11 | 70 | HB4 | A53-B | 400 | STD |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
42 | #14 GT header supply | PGB2 | 496.328 | 11.0466 | 10.0336 | 55 | 521.1444 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
43 | SWAS for #14 HRSG supply | PGB2 | 15.5318 | 11.0466 | 10.0336 | 55 | 16.3083 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 3.31 | SCH20 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
44 | GT Generator Cooler supply | PGB2 | 468.9017 | 11.0466 | 10.0336 | 55 | 492.3468 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 2.97 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y
45 | #14 GT sub header1 supply | PGB2 | 11.8946 | 11.0466 | 10.0336 | 55 | 12.4893 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A216-WCB | 13CR/STL | BB OS&Y
46 | GT Gas Dryer Cooler supply | PGB2 | 0.68812 | 11.0466 | 10.0336 | 55 | 0.72252 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 25 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A105 | 13CR/STL | BB OS&Y
47 | GT LCI Cooler supply | PGB2 | 11.2065 | 11.0466 | 10.0336 | 55 | 11.7668 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A216-WCB | 13CR/STL | BB OS&Y
48 | GT Lube Oil Cooler supply | PGB2 | 223.1461 | 11.0466 | 10.0336 | 55 | 234.3034 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
49 | GT Lube Oil Cooler Bypass | PGB2 | 281.1444 | 11.0466 | 10.0336 | 55 | 295.2016 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
50 | #15 GT header supply | PGB2 | 496.328 | 11.0466 | 10.0336 | 55 | 521.1444 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A105 | 13CR/STL | BB OS&Y
51 | GT Generator Cooler supply | PGB2 | 468.9017 | 11.0466 | 10.0336 | 55 | 492.3468 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 1.98 | SCH80 | 3.73 | A216-WCB | 13CR/STL | BB OS&Y
52 | #15 GT sub header1 supply | PGB2 | 11.8946 | 11.0466 | 10.0336 | 55 | 12.4893 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.43 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
53 | GT Gas Dryer Cooler supply | PGB2 | 0.68812 | 11.0466 | 10.0336 | 55 | 0.72252 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 25 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
54 | GT LCI Cooler supply | PGB2 | 11.2065 | 11.0466 | 10.0336 | 55 | 11.7668 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A105 | 13CR/STL | BB OS&Y
55 | GT Lube Oil Cooler supply | PGB2 | 223.1461 | 11.0466 | 10.0336 | 55 | 234.3034 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1
56 | GT Lube Oil Cooler Bypass | PGB2 | 281.1444 | 11.0466 | 10.0336 | 55 | 295.2016 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1
57 | QMS header return | PGB1 | 25.5586 | 11.0466 | 10.0336 | 60.2967 | 26.8365 | 12.013 | 11 | 70 | HB4 | A53-B | 80 | 40 |  | 3 |  | 1.1
58 | QMS for Cogen return | PGB1 | 15.5318 | 11.0466 | 10.0336 | 60.2967 | 16.3083 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1
59 | QMS for TGP return | PGB1 | 10.0268 | 11.0466 | 10.0336 | 60.2967 | 10.5282 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3
60 | SWAS for Aux. Boiler return | PGB1 | 20.8401 | 11.0466 | 10.0336 | 60.2967 | 21.8821 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3
61 | Air compressor cooler return | PGB1 | 103.414 | 11.0466 | 10.0336 | 60.2967 | 108.5847 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3
62 | #13 GT header return | PGB1 | 504.2905 | 11.0466 | 10.0336 | 60.2967 | 529.505 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3
63 | SWAS for #13HRSG return | PGB1 | 23.4942 | 11.0466 | 10.0336 | 60.2967 | 24.6689 | 12.013 | 11 | 70 | HB4 | A53-B | 80 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
64 | GT Generator Cooler return | PGB1 | 468.9017 | 11.0466 | 10.0336 | 60.2967 | 492.3468 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
65 | #13 GT sub header1 return | PGB1 | 11.8946 | 11.0466 | 10.0336 | 60.2967 | 12.4893 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 2.97 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y
66 | GT Gas Dryer Cooler return | PGB1 | 0.68812 | 11.0466 | 10.0336 | 60.2967 | 0.72252 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 25 | 80 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A216-WCB | 13CR/STL | BB OS&Y
67 | GT LCI Cooler return | PGB1 | 11.2065 | 11.0466 | 10.0336 | 60.2967 | 11.7668 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A105 | 13CR/STL | BB OS&Y
68 | GT Lube Oil Cooler return | PGB1 | 223.1461 | 11.0466 | 10.0336 | 60.2967 | 234.3034 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A216-WCB | 13CR/STL | BB OS&Y
69 | Common CCW return header PGB00BR002 | PGB1 | 2420.9875 | 11.0466 | 10.0336 | 60.2967 | 2542.0369 | 12.013 | 11 | 70 | HB4 | A53-B | 600 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
70 | #Cogen & TGP BFP return | PGB1 | 109.1155 | 11.0466 | 10.0336 | 60.2967 | 114.5713 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
71 | COGEN FWP return Header | PGB1 | 84.5399 | 11.0466 | 10.0336 | 60.2967 | 88.7669 | 12.013 | 11 | 70 | HB4 | A53-B | 100 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 1.98 | SCH80 | 3.73 | A216-WCB | 13CR/STL | BB OS&Y
72 | COGEN FWP return Branch | PGB1 | 16.908 | 11.0466 | 10.0336 | 60.2967 | 17.7534 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.43 | SCH40 | 5.49 | A216-WCB | 13CR/STL | BB OS&Y
73 | TGP FWP return Header | PGB1 | 24.5756 | 11.0466 | 10.0336 | 60.2967 | 25.8043 | 12.013 | 11 | 70 | HB4 | A53-B | 80 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
74 | TGP FWP return Branch | PGB1 | 4.9151 | 11.0466 | 10.0336 | 60.2967 | 5.1609 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A105 | 13CR/STL | BB OS&Y
75 | #11 ST header return | PGB1 | 659.608 | 11.0466 | 10.0336 | 60.2967 | 692.5884 | 12.013 | 11 | 70 | HB4 | A53-B | 300 | STD |  | 3 |  | 1.1
76 | ST Generator Cooler return Header | PGB1 | 511.1716 | 11.0466 | 10.0336 | 60.2967 | 536.7302 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1
77 | ST Generator Cooler return Branch | PGB1 | 127.7929 | 11.0466 | 10.0336 | 60.2967 | 134.1826 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1
78 | #11 ST sub header1 return | PGB1 | 148.4364 | 11.0466 | 10.0336 | 60.2967 | 155.8582 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1
79 | ST Lube Oil Cooler return Header | PGB1 | 142.5382 | 11.0466 | 10.0336 | 60.2967 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3
80 | ST Lube Oil Cooler return Branch | PGB1 | 142.5382 | 11.0466 | 10.0336 | 60.2967 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3
81 | ST Hydraulic Unit Cooler return | PGB1 | 5.8981 | 11.0466 | 10.0336 | 60.2967 | 6.193 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3
82 | Common CCW return header PGB00BR003 | PGB1 | 1652.264 | 11.0466 | 10.0336 | 60.2967 | 1734.8772 | 12.013 | 11 | 70 | HB4 | A53-B | 500 | STD |  | 3
83 | #12 ST header return | PGB1 | 659.608 | 11.0466 | 10.0336 | 60.2967 | 692.5884 | 12.013 | 11 | 70 | HB4 | A53-B | 300 | STD |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
84 | ST Generator Cooler return Header | PGB1 | 511.1716 | 11.0466 | 10.0336 | 60.2967 | 536.7302 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
85 | ST Generator Cooler return Branch | PGB1 | 127.7929 | 11.0466 | 10.0336 | 60.2967 | 134.1826 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 3.31 | SCH20 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
86 | #12 ST sub header1 return | PGB1 | 148.4364 | 11.0466 | 10.0336 | 60.2967 | 155.8582 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  |  | 150 | HB4 | H | B | 4 | 1.6 | 2.97 | SCH40 | 7.11 | A216-WCB | 13CR/STL | BB OS&Y
87 | ST Lube Oil Cooler return Header | PGB1 | 142.5382 | 11.0466 | 10.0336 | 60.2967 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A216-WCB | 13CR/STL | BB OS&Y
88 | ST Lube Oil Cooler return Branch | PGB1 | 142.5382 | 11.0466 | 10.0336 | 60.2967 | 149.6652 | 12.013 | 11 | 70 | HB4 | A53-B | 150 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.78 | SCH40 | 6.55 | A105 | 13CR/STL | BB OS&Y
89 | ST Hydraulic Unit Cooler return | PGB1 | 5.8981 | 11.0466 | 10.0336 | 60.2967 | 6.193 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A216-WCB | 13CR/STL | BB OS&Y
90 | Common CCW return header PGB00BR004 | PGB1 | 992.656 | 11.0466 | 10.0336 | 60.2967 | 1042.2888 | 12.013 | 11 | 70 | HB4 | A53-B | 400 | STD |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
91 | #14 GT header return | PGB1 | 496.328 | 11.0466 | 10.0336 | 60.2967 | 521.1444 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.24 | SCH80 | 5.54 | A216-WCB | 13CR/STL | BB OS&Y
92 | SWAS for #14 HRSG return | PGB1 | 15.5318 | 11.0466 | 10.0336 | 60.2967 | 16.3083 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 2.01 | SCH80 | 3.91 | A105 | 13CR/STL | BB OS&Y
93 | GT Generator Cooler return | PGB1 | 468.9017 | 11.0466 | 10.0336 | 60.2967 | 492.3468 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 1.98 | SCH80 | 3.73 | A216-WCB | 13CR/STL | BB OS&Y
94 | #14 GT sub header1 return | PGB1 | 11.8946 | 11.0466 | 10.0336 | 60.2967 | 12.4893 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A216-WCB | 13CR/STL | BB OS&Y
95 | GT Gas Dryer Cooler return | PGB1 | 0.68812 | 11.0466 | 10.0336 | 60.2967 | 0.72252 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 25 | 80 |  | 3 |  | 1.1 | 150 | HB4 | H | B | 4 | 1.6 | 5.94 | SCH10 | 6.35 | A105 | 13CR/STL | BB OS&Y
96 | GT LCI Cooler return | PGB1 | 11.2065 | 11.0466 | 10.0336 | 60.2967 | 11.7668 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3 |  | 1.1
97 | GT Lube Oil Cooler return | PGB1 | 223.1461 | 11.0466 | 10.0336 | 60.2967 | 234.3034 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3 |  | 1.1
98 | #15 GT header return | PGB1 | 496.328 | 11.0466 | 10.0336 | 60.2967 | 521.1444 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1
99 | GT Generator Cooler return | PGB1 | 468.9017 | 11.0466 | 10.0336 | 60.2967 | 492.3468 | 12.013 | 11 | 70 | HB4 | A53-B | 250 | 40 |  | 3 |  | 1.1
100 | #15 GT sub header1 return | PGB1 | 11.8946 | 11.0466 | 10.0336 | 60.2967 | 12.4893 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 50 | 80 |  | 3
101 | GT Gas Dryer Cooler return | PGB1 | 0.68812 | 11.0466 | 10.0336 | 60.2967 | 0.72252 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 25 | 80 |  | 3
102 | GT LCI Cooler return | PGB1 | 11.2065 | 11.0466 | 10.0336 | 60.2967 | 11.7668 | 12.013 | 11 | 70 | HB4 | A106Gr.B | 40 | 80 |  | 3
103 | GT Lube Oil Cooler return | PGB1 | 223.1461 | 11.0466 | 10.0336 | 60.2967 | 234.3034 | 12.013 | 11 | 70 | HB4 | A53-B | 200 | 40 |  | 3
O | Desal Water Feed System (Desal)
1 | Desal water feed pump discharge | PAB1 | 1027.2222 | 3.5 | 2.5 | 37 | 1027.2222 | 4 | 3 | 40 | HR1 | GRP | 700 | PN10 |  | 2.7 | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake) | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake)
2 | Header to Desal Plant | PAB1 | 681.9444 | 3.5 | 2.5 | 37 | 681.9444 | 4 | 3 | 40 | HR1 | GRP | 700 | PN10 |  | 2.7 | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake) | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake)
3 | Future RO Plant | PAB1 | 296.1111 | 3.5 | 2.5 | 37 | 296.1111 | 4 | 3 | 40 | HR1 | GRP | 600 | PN10 |  | 2.7 | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake) | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake)
4 | Screen Pump of Seawater Intake Facility | PAB1 | 20 | 3.5 | 2.5 | 37 | 20 | 4 | 3 | 40 | HR1 | GRP | 100 | PN10 |  | 2.7 | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake) | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake) | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
5 | Recirculation Line | PAB1 | 345.2778 | 3.5 | 2.5 | 37 | 345.2778 | 4 | 3 | 40 | HR1 | GRP | 500 | PN10 |  | 2.7 | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake) | 19K9-50PAB10-M05-0001_RA_Desal Feed System(Incl.Sewater intake)
[19 empty] | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
P | Potable Water System (Desal) | [17 empty] | 150 | HC1 | 0 | 1.75 | SCH5S | 3.4 | A351-CF8 | SS304/STL | BB OS&Y
1 | Desal plant to potable water storage tank(AG) |  | 981 |  | Later | 37 | 981 |  | Later | 40 |  | GRP | 450 |  |  |  |  | 2.1
2 | Desal plant to potable water storage tank(UG) |  | 981 |  | Later | 37 | 981 |  | Later | 40 |  | HDPE | 450 | [5 empty] | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
3 | Potable water storage tank to Potable water transfer pumps (to TOF)_Common | GKB1 | 61.1111 | 3.013 | 2 | 37 | 61.1111 | 4.013 | 3 | 40 | HC1 | A312TP304 | 300 |  |  | 1.8 |  | 2.1 | 150 | HC1 | 0 | 1.75 | SCH5S | 3.4 | A351-CF8 | SS304/STL | BB OS&Y
4 | Potable water transfer pumps (to TOF) suction | GKB1 | 18.0556 | 3.013 | 2 | 37 | 18.0556 | 4.013 | 3 | 40 | HC1 | A312TP304 | 150 |  |  | 1.8 |  | 2.1
5 | Potable water transfer pumps (to TOF) discharge | GKB12 | 18.0556 | 10.513 | 9.5 | 37 | 18.0556 | 12.013 | 11 | 40 |  | GRP AND HDPE | 100 |  |  | 2.25 |  |  | 150 | HC1 | 0 | 2.07 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
6 | Potable water transfer pumps (to TOF) header | GKB3 | 36.1111 | 10.513 | 9.5 | 37 | 36.1111 | 12.013 | 11 | 40 | HC1 | A312TP304 | 200 |  |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
7 | Potable water transfer pumps (to TOF) Min. Recirculation | GKB3 | 10.8333 | 10.513 | 9.5 | 37 | 10.8333 | 12.013 | 11 | 40 | HC1 | A312TP304 | 80 |  |  | 2.25 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
8 | Potable water transfer pumps (to TOF) to Internal Use | GKB13 | 1.3889 | 10.513 | 9.5 | 37 | 1.3889 | 12.013 | 11 | 40 |  | GRP AND HDPE | 50 |  |  | 2.25 |  |  | 150 | HC1 | 0 | 1.4 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
9 | Potable water delivery pumps (to Tanajib Community) suction | GKB2 | 30.5556 | 3.013 | 2 | 37 | 30.5556 | 4.013 | 3 | 40 | HC1 | A312TP304 | 200 |  |  | 1.8 |  | 2.1
10 | Potable water delivery pumps (to Tanajib Community) discharge | GKB2 | 30.5556 | 8.713 | 7.7 | 37 | 30.5556 | 10.013 | 9 | 40 | HC1 | A312TP304 | 150 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
11 | Potable water delivery pumps (to Tanajib Community) header | GKB4 | 61.1111 | 8.713 | 7.7 | 37 | 61.1111 | 10.013 | 9 | 40 | HC1 | A312TP304 | 200 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
12 | Potable water transfer pumps (to T.C) Min. Recirculation | GKB4 | 18.3333 | 8.713 | 7.7 | 37 | 18.3333 | 10.013 | 9 | 40 | HC1 | A312TP304 | 100 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 0.73 | SCH5S | 2.11 | A351-CF8 | SS304/STL | BB OS&Y
13 | Potable water storage tank to Potable water delivery pumps (to Cogen/Zuluf) | GKB14 | 960 | 3.013 | 2 | 37 | 960 | 4.013 | 3 | 40 |  | GRP AND HDPE | 500 |  |  | 2.3 |  |  | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
14 | Potable water delivery pumps (to Cogen/Zuluf) suction | GKB2 | 480 | 3.013 | 2 | 37 | 480 | 4.013 | 3 | 40 | HC1 | A312TP304 | 350 |  |  | 1.8 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
15 | Potable water delivery pumps (to Cogen/Zuluf) discharge | GKB2 | 480 | 11.413 | 10.4 | 37 | 480 | 12.513 | 11.5 | 40 | HC1 | A312TP304 | 300 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
16 | Potable water delivery pumps (to Cogen/Zuluf) header | GKB5 | 960 | 11.413 | 10.4 | 37 | 960 | 12.513 | 11.5 | 40 |  | GRP AND HDPE | 450 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
17 | Potable water delivery pumps (to Cogen/Zuluf) header (UG)_To Cogen | GKB5 | 150.4111 | 11.413 | 10.4 | 37 | 150.4111 | 12.513 | 11.5 | 40 |  | GRP AND HDPE | 630 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 0.73 | SCH5S | 2.11 | A351-CF8 | SS304/STL | BB OS&Y
18 | Potable water delivery pumps (to Cogen/Zuluf) header (UG)_To Zuluf | GKB15 | 115.7417 | 11.413 | 10.4 | 37 | 115.7417 | 12.513 | 11.5 | 40 |  | GRP AND HDPE | 400 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
19 | Potable water transfer pumps (to Congen) Min. Recirculation | GKB2 | 288 | 11.413 | 10.4 | 37 | 288 | 12.513 | 11.5 | 40 | HC1 | A312TP304 | 250 |  |  | 2.3 |  | 2.1 | 150 | HC1 | 0 | 1.08 | SCH5S | 2.77 | A351-CF8 | SS304/STL | BB OS&Y
[19 empty] | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
Q | Chemical Dosing System | [17 empty] | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
1 | Phosphate dosing to HRSG HHP Drum | QCC1 |  | 140 | 138.987 | AMB | 0 | 161 | 159.987 | AMB | DD1 | A312TP316 | 25 | PN16 |  | 2.7 |  | 2.1 | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
2 | Phosphate dosing to HRSG LP Drum | QCC2 |  | 8.6 | 7.587 | AMB | 0 | 10 | 8.987 | AMB | HD1 | A312TP316 | 25 | PN16 |  | 2.7 |  | 2.1 | 150 | HC1 | 0 | 2.27 | SCH5S | 3.96 | A351-CF8 | SS304/STL | BB OS&Y
3 | Phosphate dosing to Auxiliary Boiler Drum | QCC3 |  | 142 | 140.987 | AMB | 0 | 164 | 162.987 | AMB | DD1 | A312TP316 | 25 | PN16 |  | 2.7 |  | 2.1
4 | Ammonia dosing to Feedwater pump suction | QCB1 |  | 4 | 2.987 | AMB | 0 | 5 | 3.987 | AMB | HD1 | A312TP316 | 25 | PN16 |  | 2.7 |  | 2.1
5 | Ammonia dosing to CPP downstream | QCB2 |  | 15 | 13.987 | AMB | 0 | 18 | 16.987 | AMB | HD1 | A312TP316 | 25 | PN16 |  | 2.7 |  | 2.1
6 | Oxygen scavenger dosing to Feedwater pump suction | QCA1 |  | 4 | 2.987 | AMB | 0 | 5 | 3.987 | AMB | HD1 | A312TP316 | 25 | PN16 |  | 2.7 |  | 2.1
R | Sampling System
1 | #13 HP drum |  |  | 148 | 146.987 | 342 |  |  | 161.6857 | 352 |  | A312TP304 | 20 |  |  | P | 3
2 | #13 HP saturated steam |  |  | 145 | 143.987 | 342 |  |  | 161.6857 | 352 |  | A312TP304 | 20 |  |  | P | 3
3 | #13 HP superheated steam |  |  | 143.3 | 142.287 | 567.1 |  |  | 156.5157 | 577.1 |  | A312TP304 | 20 |  |  | P | 3
4 | #13 LP drum |  |  | 9.05 | 8.037 | 176 |  |  | 8.8407 | 186 |  | A312TP304 | 20 |  |  | P | 3
5 | #13 LP saturated steam |  |  | 8.8 | 7.787 | 210 |  |  | 8.5657 | 220 |  | A312TP304 | 20 |  |  | P | 3
6 | #13 LP superheated steam |  |  | 8.6 | 7.587 | 212 |  |  | 8.3457 | 222 |  | A312TP304 | 20 |  |  | P | 3
7 | #16 Aux. Boiler drum |  |  |  | 144 | 340 |  |  | 159.3 | 350 |  | A312TP304 | 20 |  |  | P | 3
8 | #16 Aux. Boiler saurated steam |  |  |  | 144 | 340 |  |  | 159.3 | 350 |  | A312TP304 | 20 |  |  | P | 3
9 | #16 Aux. Boiler superheated |  |  |  | 144 | 567 |  |  | 159.3 | 573 |  | A312TP304 | 20 |  |  | P | 3
10 | #17 Aux. Boiler drum |  |  |  | 144 | 340 |  |  | 159.3 | 350 |  | A312TP304 | 20 |  |  | P | 3
11 | #17 Aux. Boiler saurated steam |  |  |  | 144 | 340 |  |  | 159.3 | 350 |  | A312TP304 | 20 |  |  | P | 3
12 | #17 Aux. Boiler superheated |  |  |  | 144 | 567 |  |  | 159.3 | 573 |  | A312TP304 | 20 |  |  | P | 3
13 | From CEP sampling |  |  | 14.2 | 13.187 | 93.5 |  | 20 | 18.987 | 100 |  | A312TP304 | 20 |  |  | P | 3
14 | From condensate return sampling |  |  | 19.8 | 18.787 | 54 |  | 18.013 | 17 | 60 |  | A312TP304 | 20 |  |  | N | 3
15 | From FWP TGP pump discharge |  |  | 83.913 | 82.9 | 108.3 |  | 94 | 92.987 | 185 |  | A312TP304 | 20 |  |  | P | 3
16 | From potable water transfer pump to TGP (Cogen) |  |  | 12.613 | 11.6 | 37 |  | 18.013 | 17 | 40 |  | A312TP304 | 20 |  |  | N | 3
17 | From Demin. Water transfer pump to TGP (Cogen) |  |  | 11.613 | 10.6 | 37 |  | 14.013 | 13 | 55 |  | A312TP304 | 20 |  |  | N | 3
18 | From potable water transfer pump to TOF (Desal) |  |  | 5.8 | 4.787 | 37 |  |  | 10 | 50 |  | A312TP304 | 20 |  |  | N | 3
19 | From potable water transfer pump to TC (Desal) |  |  | 7.4 | 6.387 | 37 |  |  | 12 | 50 |  | A312TP304 | 20 |  |  | N | 3
18 | From potable water transfer pump to Cogen/Zuluf(Desal) |  |  | 7.4 | 6.387 | 37 |  |  | 3 | 50 |  | A312TP304 | 20 |  |  | N | 3

## VALVE LIST (COGEN&DESAL)_이기훈프로 (hidden)
I&C VALVE LIST
PROJECT : TANAJIB IPP
DOC NO. : 19K9-20CZF00-J22-0001
DESCRIPTION : I&C VALVE
NO. | P&ID | SYSTEM | TYPE | KKS TAG | DESCRIPTION | FLUID | LINE SIZE | LINE SPEC | SPECIFICATION | [12 empty] | VALVE |  | ACTUATOR |  | EXPLOSION PROOF | SCOPE OF SUPPLY | Trillium Body Size | Trillium | REMARK
[9 empty] | ACTUATOR TYPE | BODY TYPE | FAIL POSITION | TRAVEL TIME | LEAKAGE CLASS | SIZE (DN) | BODY MATERIAL | TRIM MATERIAL | INTERNAL COATING | VALVE RATING | END CONNECTION | DISC/PLUG TYPE | BONNET TYPE | MAKER | MODEL NO. | MAKER | MODEL NO.
67 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | CV | 21NAA10AA101 | #21 LP STEAM HEADER PCV | STEAM | 300 | HB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS V | 300 | A216-WCB | 13CR/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 12" | Pneumatic Cylinder Double
68 | 19K9-20NAA10-M05-0002 | LP STEAM HEADER SYSTEM | CV | 22NAA10AA101 | #22 LP STEAM HEADER PCV | STEAM | 300 | HB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS V | 300 | A216-WCB | 13CR/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 12" | Pneumatic Cylinder Double
73 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | CV | 21LBR13AA101 | #21 HP STEAM HEADER TO AUX STEAM HEADER PCV | STEAM | 80/200 | FB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 600 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
77 | 19K9-20LBG10-M05-0001 | AUXILIARY STEAM SYSTEM | CV | 22LBR13AA101 | #22 HP STEAM HEADER TO AUX STEAM HEADER PCV | STEAM | 80/200 | FB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 600 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
88 | 19K9-11LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 11 | CV | 11GHB01AA101 | #11 CLEAN DRAIN TO WASTE WATER TREATMENT SYSTEM TCV | WATER | 150 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
91 | 19K9-12LCM10-M05-0001 | CLEAN DRAIN SYSTEM - UNIT 12 | CV | 12GHB01AA101 | #12 CLEAN DRAIN TO WASTE WATER TREATMENT SYSTEM TCV | WATER | 150 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
104 | 19K9-11LCA10-M05-0001 | CONDENSATE SYSTEM - UNIT 11 | CV | 11GHC01AA101 | #11 AIR COOLED CONDENSER CONDENSATE COLLECTION TANK INITIAL FILL & ENERGENCY MAKEUP LCV | WATER | 100 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
111 | 19K9-12LCA10-M05-0001 | CONDENSATE SYSTEM - UNIT 12 | CV | 12GHC01AA101 | #12 AIR COOLED CONDENSER CONDENSATE COLLECTION TANK INITIAL FILL & ENERGENCY MAKEUP LCV | WATER | 100 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
| 19K9-11LCA10-M05-0001 | CONDENSATE SYSTEM - UNIT 11 | CV | 11GHC01AA102 | #11 AIR COOLED CONDENSER CONDENSATE COLLECTION TANK NORMAL MAKEUP LCV | WATER | 25 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 25 | A182-F304 | SS304/STL | Stellite Hardfacing | 600 | SW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
| 19K9-12LCA10-M05-0001 | CONDENSATE SYSTEM - UNIT 12 | CV | 12GHC01AA102 | #12 AIR COOLED CONDENSER CONDENSATE COLLECTION TANK NORMAL MAKEUP LCV | WATER | 25 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 25 | A182-F304 | SS304/STL | Stellite Hardfacing | 600 | SW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
107 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | CV | 11LCA15AA101 | #11 CONDENSATE DUMP LCV | WATER | 80 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
114 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | CV | 12LCA15AA101 | #12 CONDENSATE DUMP LCV | WATER | 80 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
108 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | CV | 11LCA14AA101 | #11 CEP MINIMUM RECIRCULATION FCV | WATER | 100 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
115 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | CV | 12LCA14AA101 | #12 CEP MINIMUM RECIRCULATION FCV | WATER | 100 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
109 | 19K9-11LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 11 | CV | 11LCA10AA101 | #11 CEP DISCHARGE HEADER AIR COOLED CONDENSER CONDENSATE COLLECTION TANK LCV | WATER | 250 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 200 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 8"
116 | 19K9-12LCA10-M05-0002 | CONDENSATE SYSTEM - UNIT 12 | CV | 12LCA10AA101 | #12 CEP DISCHARGE HEADER AIR COOLED CONDENSER CONDENSATE COLLECTION TANK LCV | WATER | 250 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 200 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
123 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | CV | 20LCP30AA101 | CONDENSATE SUPPLY PUMP MINIMUM RECIRCULATION FCV | WATER | 250 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 200 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 8"
124 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | CV | 20LCP31AA101 | CONDENSATE SUPPLY PUMP DISCHARGE HEADER PCV 1 | WATER | 450 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 350 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 14" | Pneumatic Cylinder Double
125 | 19K9-20LCP10-M05-0002 | CODENSATE SYEYEM - COMMON | CV | 20LCP32AA101 | CONDENSATE SUPPLY PUMP DISCHARGE HEADER PCV 2 | WATER | 450 | GB2 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 350 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 14" | Pneumatic Cylinder Double
129 | 19K9-20LCP10-M05-0003 | CODENSATE SYEYEM - COMMON | CV | 20GHC40AA101 | DEMIN WATER MAKEUP FCV 1 | WATER | 150 | GC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
130 | 19K9-20LCP10-M05-0003 | CODENSATE SYEYEM - COMMON | CV | 20GHC40AA102 | DEMIN WATER MAKEUP FCV 2 | WATER | 150 | GC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
224 | 19K9-20LAB00-M05-0001 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | CV | 20GHC60AA101 | DEMINERALIZED WATER TO DEAERATOR A LCV | WATER | 100 | GC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 80 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
225 | 19K9-20LAB00-M05-0002 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | CV | 20GHC60AA102 | DEMINERALIZED WATER TO DEAERATOR B LCV | WATER | 100 | GC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 80 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
226 | 19K9-20LAB00-M05-0003 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | CV | 20GHC60AA103 | DEMINERALIZED WATER TO DEAERATOR C LCV | WATER | 100 | GC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 80 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
133 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | CV | 20LCA31AA101 | CONDENSATED WATER FROM PRE-HEAT EXCHANGER TO DEAERATOR A LCV | WATER | 500 | GC3 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 400 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 16" | Pneumatic Cylinder Double
142 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | CV | 20LCA32AA101 | CONDENSATED WATER FROM PRE-HEAT EXCHANGER TO DEAERATOR B LCV | WATER | 500 | GC3 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 400 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
151 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | CV | 20LCA33AA101 | CONDENSATED WATER FROM PRE-HEAT EXCHANGER TO DEAERATOR C LCV | WATER | 500 | GC3 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 400 | A351-CF8 | SS304/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
134 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | CV | 20LBG11AA101 | DEAERATOR & FEEDWATER STORAGE TANK A PEGGING STEAM PCV | WATER | 150/400 | GB4 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
143 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | CV | 20LBG12AA101 | DEAERATOR & FEEDWATER STORAGE TANK B PEGGING STEAM PCV | WATER | 150/400 | GB4 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
152 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | CV | 20LBG13AA101 | DEAERATOR & FEEDWATER STORAGE TANK C PEGGING STEAM PCV | WATER | 150/400 | GB4 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
136 | 19K9-20LAB00-M05-0001 | FEEDWATER SYSTEM | CV | 20LAD01AA101 | DEAERATOR & FEEDWATER STORAGE TANK A HOT WATER INLET PCV | WATER | 150/500 | GB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
145 | 19K9-20LAB00-M05-0002 | FEEDWATER SYSTEM | CV | 20LAD02AA101 | DEAERATOR & FEEDWATER STORAGE TANK B HOT WATER INLET PCV | WATER | 150/500 | GB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
154 | 19K9-20LAB00-M05-0003 | FEEDWATER SYSTEM | CV | 20LAD03AA101 | DEAERATOR & FEEDWATER STORAGE TANK C HOT WATER INLET PCV | WATER | 150/500 | GB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 100 | A216-WCB | 13CR/STL | Stellite Hardfacing | 300 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
167 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | CV | 20LAB41AA101 | COGEN FWP A MINIMUM RECIRCULATION FCV | WATER | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A216-WCC | 13CR/STL | Stellite Hardfacing | 1500 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4" | Pneumatic Cylinder Double
170 | 19K9-20LAB00-M05-0005 | FEEDWATER SYSTEM - COGEN | CV | 20LAB42AA101 | COGEN FWP B MINIMUM RECIRCULATION FCV | WATER | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A216-WCC | 13CR/STL | Stellite Hardfacing | 1500 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4" | Pneumatic Cylinder Double
173 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | CV | 20LAB43AA101 | COGEN FWP C MINIMUM RECIRCULATION FCV | WATER | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A216-WCC | 13CR/STL | Stellite Hardfacing | 1500 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4" | Pneumatic Cylinder Double
176 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | CV | 20LAB44AA101 | COGEN FWP D MINIMUM RECIRCULATION FCV | WATER | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A216-WCC | 13CR/STL | Stellite Hardfacing | 1500 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4" | Pneumatic Cylinder Double
179 | 19K9-20LAB00-M05-0006 | FEEDWATER SYSTEM - COGEN | CV | 20LAB45AA101 | COGEN FWP E MINIMUM RECIRCULATION FCV | WATER | 150 | DB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A216-WCC | 13CR/STL | Stellite Hardfacing | 1500 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4" | Pneumatic Cylinder Double
182 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB21AA101 | TGP FWP A MINIMUM RECIRCULATION FCV | WATER | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
185 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB22AA101 | TGP FWP B MINIMUM RECIRCULATION FCV | WATER | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
192 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | CV | 25LAB23AA101 | TGP FWP C MINIMUM RECIRCULATION FCV | WATER | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
195 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | CV | 25LAB24AA101 | TGP FWP D MINIMUM RECIRCULATION FCV | WATER | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
198 | 19K9-25LAB00-M05-0008 | FEEDWATER SYSTEM - TGP | CV | 25LAB25AA101 | TGP FWP E MINIMUM RECIRCULATION FCV | WATER | 80 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I
187 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB41AA112 | TGP FWP DISCHARGE HEADER TO TGP PCV 1 | WATER | 250 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 200 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 8"
189 | 19K9-25LAB00-M05-0007 | FEEDWATER SYSTEM - TGP | CV | 25LAB42AA112 | TGP FWP DISCHARGE HEADER TO TGP PCV 2 | WATER | 250 | EB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 200 | A216-WCB | 13CR/STL | Stellite Hardfacing | 900 | BW | PLUG TYPE | PSB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 8"
215 | 19K9-20EGD00-M05-0001 | LIQUID PENTANE SUPPLY SYSTEM | CV | 20LBR80AA101 | PENTANE GAS OUTLET TCV | CONDENSATE | 80 | FB1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 50 | A105 | 13CR/STL | Stellite Hardfacing | 600 | SW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | YES | SCT_I | 2"
219 | 19K9-20GKB10-M05-0001 | POTABLE WATER DISTRIBUTION SYSTEM (COGEN) | CV | 20GKB20AA101 | POTABLE WATER TRANSFER PUMP (TO TGP) MINIMUM RECIRCULATION PCV | WATER | 150 | HD1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 100 | A351-CF8 | SS304/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 4"
223 | 19K9-20GHC10-M05-0001 | DEMINERALIZED WATER DISTRIBUTION SYSTEM | CV | 20GHC20AA101 | DEMINERALIZED WATER TRANSFER PUMP (TO TGP) MINIMUM RECIRCULATION PCV | WATER | 25 | HC1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 25 | A182-F304 | SS304/STL | Stellite Hardfacing | 600 | SW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 1"
3 | 19K9-50PAB10-M05-0001 | DESAL FEED SYSTEM (INCL. SEAWATER INTAKE) | CV | 50PAB20AA101 | DESAL WATER FEED PUMP MINIMUM RE-CIRCULATION PCV | SEA WATER | 500 | HR3 | PNEUMATIC OPERATED (CONTROL) | BUTTERFLY | FAIL LOCK | LATER | CLASS IV | 500 | A995-5A | - | RUBBERLINED | 150 | DOUBLE FLANGED | ECCENTRIC, DOUBLE OFFSET | DOUBLE FLANGED | LATER | LATER | LATER | LATER | N/A | SCT_I | 20" | Pneumatic Cylinder Double
6 | 19K9-50GKB10-M05-0001 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB35AA101 | POTABLE WATER TRANSFER PUMP (TO TOF) MINIMUM RECIRCULATION PCV | WATER | 80 | HR1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | FLANGED FF | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
7 | 19K9-50GKB10-M05-0001 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB30AA101 | POTABLE WATER TRANSFER PUMP DISCHARGE TO TOF FCV 1 | WATER | 200 | HR1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 200 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | FLANGED FF | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 8"
8 | 19K9-50GKB10-M05-0001 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB30AA102 | POTABLE WATER TRANSFER PUMP DISCHARGE TO TOF FCV 2 | WATER | 200 | HR1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 200 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | FLANGED FF | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 8"
9 | 19K9-50GKB10-M05-0002 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB45AA101 | POTABLE WATER TRANSFER PUMP (TO TANAJIB COMMUNITY) MINIMUM RECIRCULATION PCV | WATER | 100 | HR1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 80 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | FLANGED FF | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 3"
10 | 19K9-50GKB10-M05-0003 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB55AA102 | POTABLE WATER TRANSFER PUMP (TO COGEN/ZULUF) MINIMUM RECIRCULATION PCV | WATER | 250 | HR1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL OPEN | LATER | CLASS IV | 150 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | FLANGED FF | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 6"
11 | 19K9-50GKB10-M05-0003 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB60AA101 | POTABLE WATER TRANSFER PUMP DISCHARGE TO ZULUF FCV 1 | WATER | 350 | HD1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 250 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 10"
12 | 19K9-50GKB10-M05-0003 | POTABLE WATER TRANSFER SYSTEM (DESAL) | CV | 50GKB60AA102 | POTABLE WATER TRANSFER PUMP DISCHARGE TO ZULUF FCV 2 | WATER | 350 | HD1 | PNEUMATIC OPERATED (CONTROL) | GLOBE | FAIL CLOSE | LATER | CLASS IV | 250 | A351-CF8M | SS316/STL | Stellite Hardfacing | 150 | BW | PLUG TYPE | BB OS&Y | LATER | LATER | LATER | LATER | N/A | SCT_I | 10"

## Sheet2 (hidden)
NO | TAG | AREA | HOLD
1 | 50GMA12CP501 | AREA-1
2 | 50GMA11CP501 | AREA-1
3 | 50GMA52CP501 | AREA-1
4 | 50GMA51CP501 | AREA-1
5 | 50GQA20CL101 | AREA-1
1 | 50GKB01CL001A | AREA-2 | HOLD
2 | 50GKB01CL001B | AREA-2 | HOLD
51 | 50GKB00AA202 | AREA-2
52 | 50GKB45AA101 | AREA-2
1 | 50GKB30CP002A | AREA-2-1
2 | 50GKB30CP002B | AREA-2-1
3 | 50GKB30CT001 | AREA-2-1
4 | 50GKB30CQ001 | AREA-2-1
5 | 50GKB50CT001 | AREA-2-1
6 | 50GKB50CQ001 | AREA-2-1
7 | 50GKB40CT001 | AREA-2-1
8 | 50GKB40CQ001 | AREA-2-1
9 | 50GKB30CP001A | AREA-2-1
10 | 50GKB30CP001B | AREA-2-1
11 | 50GKB50CP001A | AREA-2-1
12 | 50GKB50CP001B | AREA-2-1
13 | 50GKB40CP001A | AREA-2-1
14 | 50GKB40CP001B | AREA-2-1
15 | 50GKB34CP503 | AREA-2-1
16 | 50GKB34CP502 | AREA-2-1
17 | 50GKB34CP501 | AREA-2-1
18 | 50GKB33CP503 | AREA-2-1
19 | 50GKB33CP502 | AREA-2-1
20 | 50GKB33CP501 | AREA-2-1
21 | 50GKB32CP503 | AREA-2-1
22 | 50GKB32CP502 | AREA-2-1
23 | 50GKB32CP501 | AREA-2-1
24 | 50GKB31CP503 | AREA-2-1
25 | 50GKB31CP502 | AREA-2-1
26 | 50GKB31CP501 | AREA-2-1
27 | 50GKB54CP503 | AREA-2-1
28 | 50GKB54CP502 | AREA-2-1
29 | 50GKB54CP501 | AREA-2-1
30 | 50GKB53CP503 | AREA-2-1
31 | 50GKB53CP502 | AREA-2-1
32 | 50GKB53CP501 | AREA-2-1
33 | 50GKB52CP503 | AREA-2-1
34 | 50GKB52CP502 | AREA-2-1
35 | 50GKB52CP501 | AREA-2-1
36 | 50GKB51CP503 | AREA-2-1
37 | 50GKB51CP502 | AREA-2-1
38 | 50GKB51CP501 | AREA-2-1
39 | 50GKB60CF001A | AREA-2-1 | HOLD
40 | 50GKB60CF001B | AREA-2-1 | HOLD
41 | 50GKB60CF601 | AREA-2-1 | HOLD
51 | 50GKB30AA102 | AREA-2-1
52 | 50GKB30AA101 | AREA-2-1
53 | 50GKB35AA101 | AREA-2-1
54 | 50GKB55AA102 | AREA-2-1
55 | 50GKB60AA101 | AREA-2-1 | HOLD
56 | 50GKB60AA102 | AREA-2-1 | HOLD
1 | 50GKB44CP503 | AREA-3
2 | 50GKB44CP502 | AREA-3
3 | 50GKB44CP501 | AREA-3
4 | 50GKB43CP503 | AREA-3
5 | 50GKB43CP502 | AREA-3
6 | 50GKB43CP501 | AREA-3
7 | 50GKB42CP503 | AREA-3
8 | 50GKB42CP502 | AREA-3
9 | 50GKB42CP501 | AREA-3
10 | 50GKB41CP503 | AREA-3
11 | 50GKB41CP502 | AREA-3
12 | 50GKB41CP501 | AREA-3
13 | 50GKB02CL001A | AREA-3 | HOLD
14 | 50GKB02CL001B | AREA-3 | HOLD
51 | 50GKB00AA201 | AREA-3
1 | 50GMA42CP501 | AREA-4
2 | 50GMA41CP501 | AREA-4
3 | 50SCB01CP001 | AREA-4
4 | 50SCB01CT001 | AREA-4
5 | 50QFB00CT001 | AREA-4 | HOLD
6 | 50QFB01CT001 | AREA-4 | HOLD
7 | 50QFB00CP001A | AREA-4 | HOLD
8 | 50QFB01CP001B | AREA-4 | HOLD
9 | 50GUA12CP501 | AREA-4
10 | 50GUA11CP501 | AREA-4
11 | 50GMB10CP501 | AREA-4
12 | 50GMA22CP501 | AREA-4
13 | 50GMA21CP501 | AREA-4
14 | 50GQA10CL101 | AREA-4 | HOLD
15 | 50QFB01CP501 | AREA-4 | HOLD
51 | 50SCB01AA251 | AREA-4
1 | 50GMA32CP501 | AREA-5
2 | 50GMA31CP501 | AREA-5
3 | 50PAB10CP001A | AREA-5
4 | 50PAB10CP001B | AREA-5
5 | 50PAB02CP001 | AREA-5
6 | 50PAB02CP501 | AREA-5
7 | 50PAB01CP001 | AREA-5
8 | 50PAB01CP501 | AREA-5
51 | 50PAB02AA201 | AREA-5
52 | 50PAB01AA201 | AREA-5
53 | 50PAB20AA101 | AREA-5